## Slide 1: IPI (ınıtıal PRODUCT INFORMATION) heat-pump mını vrf outdoor unıts (8  18 KW)

## Slide 2: Table of Contents
Initial Product Information : AF4300A (8-18kW)
Product overview
Nomenclature
Technical specifications
Part Numbers
Compatibility
System architecture
Features and Functions
Electrical specifications
Sound Levels

## Slide 3: Product Overview
Initial Product Information : AF4300A (8-18kW)
Extended line-up up to 18 kW with same structure
Full DC inverter techonology
Low stand-by power consumption, just 3,5 W
High Efficiency : SEER up to 7,8 and SCOP up to 4,9
Up to 15% higher SEER and 20% higher SCOP compared to predecessor units
New refrigerant with lower GWP – R-32
1-ph or 3-ph power supply options
Extended operation range : Cooling -15º+52ºC DB, Heating -20+30ºC DB
Totally new industrial design, new structure, COMPACT & slim – Single fan only
Higher combination ratio – up to 160%
Extended piping lenghts up to 300m (total), 120m (max)
Low unit height < 1 meter enabling convenient installations at field
New communication protocol – SuperLink
PCB design is improved for increased electrical safety (SELV PCB)
Low noise levels with DC inverter fan including night silent mode option
Refrigerant leakage detection sensor connection via dry contact (in case needed)
Refrigerant shut-off device connection possibility (In case needed)
Footnote:
GWP:Global warming potential
SELV: Safety extra low voltage
SEER:Seasonal energy efficiency ratio
SCOP:Seasonal coeeficient of perfomance

## Slide 4: Nomenclature
Initial Product Information : AF4300A (8-18kW)
1 Category name | 2 Value Level | 3 Group Name
Air Flux | 4300 | A / W
Variable refrigerant flow air conditioning unit
4300: Mini VRF units, 2-pipe, up to +55ºC 5300: Maxi VRF units, 2-pipe, up to +48ºC
6300: Maxi VRF units, 3-pipe, up to +48ºC
(i) : stands for connected device
-1 = Single phase
-3 = Three phase
Product Type
C = unit can be combined - = for single use
Example :
Product name : Air Flux 4300 A
Product line : AF4300A
Product type : AF4300A 12 -1
Product name
1 Category name | 2 Value Level | 3 Group Name | 4 Output / Generation | 6 Power supply
AF | 4300 | A / W | 50 C | - 3
Product Line
A: Air based system
W Water based system
12 = 12 kW heat output

## Slide 5: Line-up
Internal | Thermotechnology | TT-CA/PRM-Denizalp | 15/06/2018
© Robert Bosch GmbH 2016. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
6
Initial Product Information : AF4300A (8-18kW)
Product type | Power supply | Rated cooling capacity | Rated heating capacity | Maximum number of connected indoor units | Unit Structure
 | V/ph/Hz | kW | kW | pcs | 
AF4300A 8-1 | 220~240/1/50 | 7,2 | 7,2 | 5 | 
AF4300A 10-1 | 220~240/1/50 | 9 | 9 | 6 | 
AF4300A 12-1 | 220~240/1/50 | 12,3 | 12,3 | 8 | 
AF4300A 14-1 | 220~240/1/50 | 14 | 14 | 10 | 
AF4300A 16-1 | 220~240/1/50 | 15,5 | 15,5 | 11 | 
AF4300A 18-1 |  | 17,5 | 17,5 | 12 | 
AF4300A 12-3 | 380~415/3/50 | 12,3 | 12,3 | 8 | 
AF4300A 14-3 | 3-ph | 14 | 14 | 10 | 
AF4300A 16-3 | 3-ph | 15,5 | 15,5 | 11 | 
AF4300A 18-3 | 3-ph | 17,5 | 17,5 | 12 | 

## Slide 6: Technical Specs, 1-ph
Initial Product Information : AF4300A (8-18kW)
HP |  |  | 2 | 3 | 4 | 5 | 6 | 7
Product Type |  |  | AF4300A 8-1 | AF4300A 10-1 | AF4300A 12-1 | AF4300A 14-1 | AF4300A 16-1 | AF4300A 18-1
Power supply |  | V/N/Hz | 220~240/1/50 | 220~240/1/50 | 220~240/1/50 | 220~240/1/50 | 220~240/1/50 | 220~240/1/50
Cooling | Capacity | kW | 7,2 | 9 | 12,3 | 14 | 15,5 | 17,5
 | Power input | kW | 1,95 | 2,77 | 3,73 | 4,67 | 5,34 | 6,46
 | EER |  | 3,70 | 3,09 | 3,41 | 2,92 | 3,00 | 2,71
Heating（Rated) | Capacity | kW | 7,2 | 9 | 12,3 | 14 | 15,5 | 17,5
 | Power input | kW | 1,8 | 2,31 | 2,86 | 3,29 | 3,73 | 4,49
 | COP |  | 4,00 | 3,87 | 4,27 | 4,21 | 4,12 | 4,00
Heating（Max) | Capacity | kW | 9 | 10,8 | 14 | 16 | 17,5 | 19,5
 | Power input | kW | 2,50 | 3,18 | 3,59 | 4,21 | 4,73 | 5,57
 | COP |  | 3,6 | 3,4 | 3,9 | 3,8 | 3,7 | 3,5
SEER |  |  | 5,80 | 5,70 | 7,80 | 7,40 | 7,35 | 7,10
ηs,c |  | % | Energy class A+ | Energy class A+ | 309 | 293 | 291 | 281
SCOP |  |  | 3,80 | 3,80 | 4,90 | 4,80 | 4,70 | 4,80
ηs,h |  | % | Energy class A | Energy class A | 193 | 189 | 184 | 189
Connected indoor unit | Total capacity |  | 50 - 160 | 50 - 160 | 50 - 160 | 50 - 160 | 50 - 160 | 50 - 160
 | Maximum quantity |  | 5 | 6 | 8 | 10 | 11 | 12
Compressor | Type |  | DC inverter Rotary | DC inverter Rotary | DC inverter Rotary | DC inverter Rotary | DC inverter Rotary | DC inverter Rotary
 | Quantity |  | 1 | 1 | 1 | 1 | 1 | 1
 | Oil type |  | FW68S | FW68S | FW68S | FW68S | FW68S | FW68S
 | Start-up method |  | Soft start | Soft start | Soft start | Soft start | Soft start | Soft start

## Slide 7: Technical Specs, 1-ph
Initial Product Information : AF4300A (8-18kW)
HP |  |  | 2 | 3 | 4 | 5 | 6 | 7
Product Type |  |  | AF4300A 8-1 | AF4300A 10-1 | AF4300A 12-1 | AF4300A 14-1 | AF4300A 16-1 | AF4300A 18-1
Fan | Type |  | Propeller | Propeller | Propeller | Propeller | Propeller | Propeller
 | Motor type |  | DC inverter | DC inverter | DC inverter | DC inverter | DC inverter | DC inverter
 | Quantity |  | 1 | 1 | 1 | 1 | 1 | 1
 | Motor output | kW | 200 | 200 | 200 | 200 | 200 | 200
 | Static pressure | Pa | 0 | 0 | 0 | 0 | 0 | 0
 | Airflow rate | m3/h | 5200 | 5200 | 5000 | 5000 | 5000 | 5500
 | Drive type |  | Direct | Direct | Direct | Direct | Direct | Direct
Refrigerant | Type |  | R-32 | R-32 | R-32 | R-32 | R-32 | R-32
 | Factory charge | kg | 2 | 2 | 2,85 | 2,85 | 2,85 | 2,85
Pipe connections | Liquid pipe | mm | Φ9.5 | Φ9.5 | Φ9.5 | Φ9.5 | Φ9.5 | Φ9.5
 | Gas pipe | mm | Φ15.9 | Φ15.9 | Φ15.9 | Φ15.9 | Φ15.9 | Φ15.9
Sound pressure level |  | dB(A) | 53 | 53 | 55 | 56 | 56 | 58
Sound power level |  | dB(A) | 68 | 69 | 70 | 71 | 72 | 73
Net dimensions (W×H×D) |  | mm | 1038x864x409 | 1038x864x409 | 1038x864x409 | 1038x864x409 | 1038x864x409 | 1038x864x409
Packed dimensions (W×H×D) |  | mm | 1120x980x560 | 1120x980x560 | 1120x980x560 | 1120x980x560 | 1120x980x560 | 1120x980x560
Net weight |  | kg | 77 | 77 | 94 | 94 | 94 | 94
Gross weight |  | kg | 88 | 88 | 105 | 105 | 105 | 105
Ambient temp. operation range | Cooling | oC | -15 ~ 52 | -15 ~ 52 | -15 ~ 52 | -15 ~ 52 | -15 ~ 52 | -15 ~ 52
 | Heating | oC | -20 ~ 30 | -20 ~ 30 | -20 ~ 30 | -20 ~ 30 | -20 ~ 30 | -20 ~ 30
First branch to farthest IDU |  | m | 30 | 30 | 40 | 40 | 40 | 40
Max piping from ODU to furthest IDU |  | m | 60 | 60 | 120 | 120 | 120 | 120
Total pipe length (Actual) |  | m | 300 | 300 | 300 | 300 | 300 | 300
Max. difference in level |  | m | 30/20 | 30/20 | 50/40 | 50/40 | 50/40 | 50/40

## Slide 8: Technical Specs, 3-ph
Initial Product Information : AF4300A (8-18kW)
HP |  |  | 4 | 5 | 6 | 7
Product Type |  |  | AF4300A 12-3 | AF4300A 14-3 | AF4300A 16-3 | AF4300A 18-3
Power supply |  | V/N/Hz | 380~415/3/50 | 380~415/3/50 | 380~415/3/50 | 380~415/3/50
Cooling | Capacity | kW | 12,3 | 14 | 15,5 | 17,5
 | Power input | kW | 3,73 | 4,67 | 5,34 | 6,46
 | EER |  | 3,41 | 2,92 | 3,00 | 2,71
Heating（Rated) | Capacity | kW | 12,3 | 14 | 15,5 | 17,5
 | Power input | kW | 2,86 | 3,29 | 3,73 | 4,49
 | COP |  | 4,27 | 4,21 | 4,12 | 4,00
Heating（Max) | Capacity | kW | 14 | 16 | 17,5 | 19,5
 | Power input | kW | 3,59 | 4,21 | 4,73 | 5,57
 | COP |  | 3,9 | 3,8 | 3,7 | 3,5
SEER |  |  | 7,80 | 7,40 | 7,35 | 7,10
ηs,c |  | % | 309 | 293 | 291 | 281
SCOP |  |  | 4,90 | 4,80 | 4,70 | 4,80
ηs,h |  | % | 193 | 189 | 184 | 189
Connected indoor unit | Total capacity |  | 50 - 160 | 50 - 160 | 50 - 160 | 50 - 160
 | Maximum quantity |  | 8 | 10 | 11 | 12
Compressor | Type |  | DC inverter Rotary | DC inverter Rotary | DC inverter Rotary | DC inverter Rotary
 | Quantity |  | 1 | 1 | 1 | 1
 | Oil type |  | FW68S | FW68S | FW68S | FW68S
 | Start-up method |  | Soft start | Soft start | Soft start | Soft start

## Slide 9: Technical Specs, 3-ph
Initial Product Information : AF4300A (8-18kW)
HP |  |  | 4 | 5 | 6 | 7
Product Type |  |  | AF4300A 12-3 | AF4300A 14-3 | AF4300A 16-3 | AF4300A 18-3
Fan | Type |  | Propeller | Propeller | Propeller | Propeller
 | Motor type |  | DC inverter | DC inverter | DC inverter | DC inverter
 | Quantity |  | 1 | 1 | 1 | 1
 | Motor output | kW | 200 | 200 | 200 | 200
 | Static pressure | Pa | 0 | 0 | 0 | 0
 | Airflow rate | m3/h | 5000 | 5000 | 5000 | 5500
 | Drive type |  | Direct | Direct | Direct | Direct
Refrigerant | Type |  | R-32 | R-32 | R-32 | R-32
 | Factory charge | kg | 2,85 | 2,85 | 2,85 | 2,85
Pipe connections | Liquid pipe | mm | Φ9.5 | Φ9.5 | Φ9.5 | Φ9.5
 | Gas pipe | mm | Φ15.9 | Φ15.9 | Φ15.9 | Φ19.1
Sound pressure level |  | dB(A) | 55 | 56 | 56 | 58
Sound power level |  | dB(A) | 70 | 71 | 72 | 73
Net dimensions (W×H×D) |  | mm | 1038x864x409 | 1038x864x409 | 1038x864x409 | 1038x864x409
Packed dimensions (W×H×D) |  | mm | 1120x980x560 | 1120x980x560 | 1120x980x560 | 1120x980x560
Net weight |  | kg | 110 | 110 | 110 | 110
Gross weight |  | kg | 121 | 121 | 121 | 121
Ambient temp. operation range | Cooling | oC | -15 ~ 52 | -15 ~ 52 | -15 ~ 52 | -15 ~ 52
 | Heating | oC | -20 ~ 30 | -20 ~ 30 | -20 ~ 30 | -20 ~ 30
First branch to farthest IDU |  | m | 40 | 40 | 40 | 40
Max piping from ODU to furthest IDU |  | m | 120 | 120 | 120 | 120
Total pipe length (Actual) |  | m | 300 | 300 | 300 | 300
Max. difference in level |  | m | 50/40 | 50/40 | 50/40 | 50/40

## Slide 10: Part Numbers
Initial Product Information : AF4300A (8-18kW)
Part number | EAN Number | Family | Product Name | Product Type | SAP Description | PH Product Hierarchy
7733702217 | 4062321733254 | Outdoor unit | AF4300A | AF4300A 8-1 | Air Flux 4300 A - AF4300A 8-1 | 0T1410308600060134
7733702218 | 4062321732448 | Outdoor unit | AF4300A | AF4300A 10-1 | Air Flux 4300 A - AF4300A 10-1 | 0T1410308600060134
7733702219 | 4062321732455 | Outdoor unit | AF4300A | AF4300A 12-1 | Air Flux 4300 A - AF4300A 12-1 | 0T1410308600060134
7733702220 | 4062321732462 | Outdoor unit | AF4300A | AF4300A 14-1 | Air Flux 4300 A - AF4300A 14-1 | 0T1410308600060134
7733702221 | 4062321732479 | Outdoor unit | AF4300A | AF4300A 16-1 | Air Flux 4300 A - AF4300A 16-1 | 0T1410308600060134
7733702222 | 4062321732486 | Outdoor unit | AF4300A | AF4300A 18-1 | Air Flux 4300 A - AF4300A 16-1 | 0T1410308600060134
7733702223 | 4062321732493 | Outdoor unit | AF4300A | AF4300A 12-3 | Air Flux 4300 A - AF4300A 12-3 | 0T1410308600060134
7733702224 | 4062321732509 | Outdoor unit | AF4300A | AF4300A 14-3 | Air Flux 4300 A - AF4300A 14-3 | 0T1410308600060134
7733702225 | 4062321732516 | Outdoor unit | AF4300A | AF4300A 16-3 | Air Flux 4300 A - AF4300A 16-3 | 0T1410308600060134
7733702226 | 4062321732523 | Outdoor unit | AF4300A | AF4300A 18-3 | Air Flux 4300 A - AF4300A 18-3 | 0T1410308600060134

## Slide 11: Compatibility
Initial Product Information : AF4300A (8-18kW)
Central Controller
Outdoor Unit Family
Indoor Unit Family
Individual Controls
AF4300A
ARC C -2
max. 1 (up to 16 IDUs)
ACC MT
XYE
ARC H -2
max. 1 IDU
AF2
ARC C IR -2
max. 1 IDU
IR
X1X2
X1X2
M1M2
AF4300A outdoor units are only compatible with AF2 series VRF indoor units

## Slide 12: System Architecture
Initial Product Information : AF4300A (8-18kW)
Outdoor
Unit
Indoor Units
Room Controller
D1D2
group control
X1X2
XYE
Central Controller
IR
ACC MT
ARC C-2
ARC C-2
ARC H-2
IRC
R32 pump down kit (safety shut-off valves)
refrigerant detector (connected to IDU communication board)
X1X2
software update
After-Sales Board –settings after PCB replacement
USB
Diagnosis software
Service Tools
USB
RS485-USB converter
Bus signal repeater
motion detection sensor (standard on display panel)
display board (ducted units)
ARC C-2
M1M2

## Slide 13: Key Features : High Technology
Initial Product Information : AF4300A (8-18kW)
Super Link
Communication bus chip greatly simplifies installation and saves installation cost
Super Sense
13 sensors achieves the state of each part of the refrigerant pipeline
Full DC inverter technology
All electrical components of outdoor units are DC power supply, improving electrical efficiency and achieving energy saving
Low stand-by power consumption
The standby power consumption is as low as 3.5 Watt
60-step energy management
The system runs at 40% to 100% capacity output in 1% increasements
Precise oil control
Ensures all outdoor compressor oil is at a safe level, eliminating any compressor oil shortage problems.
Alarm output
In case of system malfunction, remote output error information reminds installer for maintenance
Fire alarm input
In case of fire, receive fire information in time and stop the system immediately to avoid serious problems

## Slide 14: New communication protocol : Super Link
Initial Product Information : AF4300A (8-18kW)
Higher immunity to interference
No polarity (M1M2 can be connected in any way)
Length (M1M2 can be up to 2000m, PQE can only support 1200m)
Allow system to keep operating although single indoor units are unplugged from power
Switching off valves in case of indoor unit power outage
More topology possible (PQE can be used in daisy chain only)
Support Any Topology Communication
In addition to the traditional daisy chain connection, the communication wire supports tree connection, star connection, ring connection and so on. The wring is exible, which greatly reduces the installation cost and has no possibility of wrong connection on site.
Daisy chain connection
Star connection Ring connection
Tree connection
Traditional daisy chain connection
AF4300A Wiring connection
AF4300A system continue to operate in case of disconnection
Super Anti-interference Capability
Special waveform restoration technology enhances anti-interference performance for more stable communication.
Anti-interference of radio
Anti-interference of high voltage
Anti-interference of equipment
Conventional filtering waveform
Distorted waveform reduction

## Slide 15: Super-Link (Option A – Common power supply)
Initial Product Information : AF4300A (8-18kW)
Picture shows the serial connection.
Super-link (M1M2) supports any connection type.
For other connection methods, please refer to the installation manuals.
The indoor units of the system must be powered by a unified power supply, and all indoor units must be powered on or off at the same time.
It is forbidden to connect M1M2 to different communication networks such as X1X2, etc. of the internal unit, otherwise the circuit board will be damaged.

## Slide 16: Super-Link (Option B – Individual power supply)
Initial Product Information : AF4300A (8-18kW)
Picture shows the serial connection.
Super-link (M1M2) supports any connection type.
It is forbidden to connect M1M2 to different communication networks such as X1X2, etc of the indoor unit.
The communication line needs to be 2x1.5mm2 and the line resistance should be less than or equal to 1.33Ω/100m
If the total distance is less than or equal to 200m and the total number of indoor units is less than or equal to 10, the bus repeater is not needed.
If the total distance is greater than 200m or the total number of indoor units is greater than 10, bus repeaters need to be added to increase the bus voltage.
The max number of indoor units in the same refrigerant system must be less than or equal to 30 units.
In the same refrigerant system, a maximum of 2 repeater devices can be installed.
The bus repeater is an optional accessory and needs to be purchased seperately.

## Slide 17: Key Features : High Comfort & Reliability
Initial Product Information : AF4300A (8-18kW)
Silent mode
5-step silent mode selections provide more freedom and convenience to match the customer needs
Intelligent defrosting technology
Calculates the time required for defrosting according to the actual system status, eliminating heat losses from unnecessary defrosting
Auto cooling-heating changeover
Automatically selects cooling or heating mode to achieve the set temperature (available in changeover priority mode)
Continuous heating in oil return mode
Oil return in heating mode does not need to convert to cooling mode, further enhancing indoor comfort (activated via menu setting)
0.1℃ control precision
Control precision of the sensor can reach 0.1℃, ensuring less room temperature fluctuation
Multiple priority modes
10 different priority modes meets the requirements of all user scenarios
Refrigerant leakage detector connection possibility
(In case needed)
Refrigerant shut-off device
connection possibility
(In case needed)

## Slide 18: Key Features : Easy Installation
Initial Product Information : AF4300A (8-18kW)
Long piping capability
Benefits for the system design, installation flexibility, as well as the less installation cost
Auto addressing
Distributes addresses to indoor units automatically, simplifying the installation
Automatic refrigerant recycling
Refrigerant can be recycled to outdoor unit or indoor units making the maintenance easier and more efficient
Digit display
4 digit 7-segment display intuitive for parameter setting, parameter check and error check
High external static pressure
Up to 35Pa ESP setting allows easy handling in various installations conditions
Arbitrary topology of communication wire
Supports any communication topology, greatly simplifies installation and reduces installation cost
2-core non-polarity communication wiring
Simplifies installation and reduces wiring failures
Long communication wiring
Communication wiring up to 2000m makes installation more flexible
Wide combination ratio
Combination ratio can be extended to 50%-160% which meets different project requirements
Manual defrosting and oil return
Improves maintenance efficiency and reduce service time

## Slide 19: Self Cleaning Function
Initial Product Information : AF4300A (8-18kW)
This feature is only available for systems running with AF2 indoor units and when the indoor units are connected to AF4300A outdoor unit.
Once the self-cleaning function is activated, all indoor units in the VRF system will start to proceed “Self Clean”. Therefore, this feature should be used for a system cleaning.
Self clean can not be used individually for some indoor units.
The self-cleaning function is de-activated in default settings of delivered units.
The self-cleaning function can be activated once from the outdoor unit during the regular maintenance by service professionals.
The self-cleaning function must be configured and started by qualified technicians.
Please get in contact with your installer/service company.
NOTE:
Self clean feature can be activated also from the infrared remote controller by the end user, if requested.
In this case, the VRF system operator must be trained by the service technician before enabling. Otherwise, the VRF system will be interrupted until self cleaning process ends.

## Slide 20: Refrigerant Temperature Setting
Initial Product Information : AF4300A (8-18kW)
It is possible to set different evaporation and condensation temperatures in case needed
First-level menu | Second-level menu | Specified menu mode | Description | Default
n6 | 0 | 0 | Evaporation temperature setting (Ke0=-3) | -
 |  | 1 | Evaporation temperature setting (Ke0=0) | 
 |  | 2 | Evaporation temperature setting (Ke0=3) | 
 |  | 3 | Evaporation temperature setting (Ke0=6) | √
 |  | 4 | Evaporation temperature setting (Ke0=7) | -
 |  | 5 | Evaporation temperature setting (Ke0=8) | 
 |  | 6 | Evaporation temperature setting (Ke0=9) | 
 |  | 7 | Evaporation temperature setting (Ke0=10) | 
 |  | 8 | Evaporation temperature setting (Ke0=11) | 
 | 2 | 0 | Condensation temperature setting (Kc0=41) | -
 |  | 1 | Condensation temperature setting (Kc0=42) | 
 |  | 2 | Condensation temperature setting (Kc0=43) | 
 |  | 3 | Condensation temperature setting (Kc0=44) | 
 |  | 4 | Condensation temperature setting (Kc0=45) | 
 |  | 5 | Condensation temperature setting (Kc0=46) | 
 |  | 6 | Condensation temperature setting (Kc0=48) | √
 |  | 7 | Condensation temperature setting (Kc0=51) | -

## Slide 21: Average SEER for the product family is 7,1
Initial Product Information : AF4300A (8-18kW)
Chart: 
| 8 Kw 1ph | 10 kW 1ph | 12 kW 1ph | 14 kW 1ph | 16 kW 1ph | 18 kW 1ph | 12 kW 3ph | 14 kW 3ph | 16 kW 3ph | 18 kW 3ph
MDCI | 5.2 | 5.1 | 7.1 | 6.9 | 6.7 | 0 | 7.1 | 6.9 | 6.7 | 6.2
AF4300A | 5.8 | 5.7 | 7.8 | 7.4 | 7.4 | 7.1 | 7.8 | 7.4 | 7.4 | 7.1
+15%
+10%
+7%
+10%
+10%
+7%
+10%
+8%
+10%
EU min. reqr. 4,8
EU min. reqr. 4,3
vs MDCI Series

## Slide 22: Average SCOP for the product family is 4,6
Initial Product Information : AF4300A (8-18kW)
Chart: 
| 8 Kw 1ph | 10 kW 1ph | 12 kW 1ph | 14 kW 1ph | 16 kW 1ph | 18 kW 1ph | 12 kW 3ph | 14 kW 3ph | 16 kW 3ph | 18 kW 3ph
MDCI | 3.8 | 3.8 | 4.2 | 4 | 4.3 | 0 | 4.2 | 4 | 4.3 | 4.1
AF4300A | 3.8 | 3.8 | 4.9 | 4.8 | 4.7 | 4.8 | 4.9 | 4.8 | 4.7 | 4.8
+17%
+9%
+20%
+17%
+9%
+20%
+17%
EU min. reqr. 3,5
EU min. reqr. 3,8
vs MDCI Series

## Slide 23: Wide Outdoor Ambient Operation Range
Initial Product Information : AF4300A (8-18kW)
-15˚C
+52˚C
Cooling mode
-20˚C
+30˚C
Heating mode
0 ˚C
5 ˚C
10 ˚C
15 ˚C
20 ˚C
25 ˚C
30 ˚C
35 ˚C
40 ˚C
45 ˚C
50 ˚C
-10˚C
-5 ˚C
-15˚C
-20˚C
55 ˚C
DB: Dry bulb temperature
WB: Wet bulb temperature

## Slide 24: Long Piping
Initial Product Information : AF4300A (8-18kW)
AF4300A – Piping Limits (m) |  |  | 8,10 kW | 12,14,16,18 kW
Piping Length | Actual total pipe length |  | 150 | 300
 | Maximum piping distance between outdoor unit and indoor unit | Actual | 50 | 100
 |  | Equivalent | 60 | 120
 | Maximum piping distance between the first branch joint and the farthest indoor unit |  | 30 | 40
Level difference | Level difference between indoor and outdoor units | Outdoor unit on top | 30 | 50
 |  | Outdoor unit below | 20 | 40
 | Level distance between indoor units |  | 15 | 15
➀ Level difference between indoor unit and outdoor unit is maximum 50 m (ODU on top)
➁ Level difference between indoor units is maximum 15 m
➂ Max piping from the first branch joint to the farthest indoor unit is maximum 40 m
➃ Longest pipe length is 120 m

## Slide 25: Piping Design
Initial Product Information : AF4300A (8-18kW)
a
N1
N3
N5
N6
N 2
N4
b
c
e
f
d
L 1
L 2
L 5
L 3
L 4
A
B
C
D
E
Maximum level difference between the
outdoor unit and indoor unit is ≤ 50 m
Maximum level difference between Indoor
units is ≤ 15 m
Maximum piping length from the first branch joint
to the farthest indoor unit is ≤ 40 m
Maximum equivalent piping length from the outdoor
unit to the farthest indoor unit is ≤ 120 m
joint
Refrigerant shut-off First branch
device(Optional)
RSD
Definition | Pipe connection position | Code
Main pipe | The pipe between the outdoor unit and the first branch joint. | L1
Indoor unit main pipe | The pipe between the branch joints. | L2~L5
Indoor unit auxiliary pipe | The pipe between the indoor unit and the nearest branch joint. | a~f
Branch joint | The joint connect with the main pipe, the indoor unit main pipe and auxiliary pipe. | A~E
Indoor unit | / | N1~N6

## Slide 26: Installation Options
Initial Product Information : AF4300A (8-18kW)
AF-BJ joints are used at installation.
Installation with joints

## Slide 27: Electrical Specifications
Initial Product Information : AF4300A (8-18kW)
Abbreviations:MCA: Minimum Circuit Amps;
TOCA: Total Over-current Amps;
MFA: Maximum Fuse Amps;
MSC: Maximum Starting Current (A);
RLA: Rated Load Amps;
FLA: Fan Load Amps.
Power Supply | Model | Outdoor Unit |  |  |  | Power Current |  |  | Compressor |  | Fan Motor | 
 | Capacity (kW) | Voltage (V) | Frequency (Hz) | Min. (V) | Max. (V) | MCA (Rated current) (A) | TOCA (A) | MFA (A) | MSC (A) | RLA (A) | Power (kW) | FLA (A)
220-240V~ 50Hz | 8 | 220-240 | 50 | 198 | 264 | 21.3 | 18 | 25 | - | 15.9 | 0.2 | 1.0
 | 10 | 220-240 | 50 | 198 | 264 | 24 | 20 | 25 | - | 17.9 | 0.2 | 1.0
220-240V~ | 12 | 220-240 | 50 | 198 | 264 | 32 | 27 | 32 | - | 24.8 | 0.2 | 1.2
50Hz | 14 | 220-240 | 50 | 198 | 264 | 35 | 29 | 40 | - | 26.8 | 0.2 | 1.2
 | 16 | 220-240 | 50 | 198 | 264 | 40 | 33 | 40 | - | 30.3 | 0.2 | 1.2
 | 18 | 220-240 | 50 | 198 | 264 | 40 | 33 | 40 | - | 30 | 0.2 | 1.5
380-415V 3N~ 50Hz | 12 | 380-415 | 50 | 342 | 440 | 14 | 13 | 20 | - | 10.4 | 0.2 | 0.6
380-415V 3N~ | 14 | 380-415 | 50 | 342 | 440 | 15 | 14 | 20 | - | 11.4 | 0.2 | 0.6
50Hz | 16 | 380-415 | 50 | 342 | 440 | 17 | 15 | 20 | - | 12.9 | 0.2 | 0.6
 | 18 | 380-415 | 50 | 342 | 440 | 17 | 15 | 20 | - | 12.9 | 0.2 | 0.7

## Slide 28: Sound Levels
Initial Product Information : AF4300A (8-18kW)
Sound Pressure Level dB(A) | 8 kW | 10 kW | 12 kW | 14 kW | 16 kW | 18 kW
Standard | 53 | 53 | 55 | 56 | 56 | 58
Noise Level 1 | 51 | 51 | 53 | 54 | 54 | 55
Noise Level 2 | 48 | 48 | 51 | 52 | 52 | 52
Noise Level 3 | 46 | 46 | 49 | 50 | 50 | 50
Noise Level 4 | 43 | 43 | 47 | 48 | 48 | 48
Noise Level 5 | 40 | 40 | 43 | 44 | 44 | 46
Available Capacity | 8kW | 10kw | 12kW | 14kW | 16kW | 18kW
Standard | 100% | 100% | 100% | 100% | 100% | 100%
Noise Level 1 | 90% | 90% | 90% | 90% | 90% | 90%
Noise Level 2 | 80% | 80% | 80% | 80% | 80% | 80%
Noise Level 3 | 70% | 70% | 70% | 70% | 70% | 70%
Noise Level 4 | 60% | 60% | 60% | 60% | 60% | 60%
Noise Level 5 | 50% | 50% | 50% | 50% | 50% | 50%
Silent mode can be activated and programmed from controllers.
Local standards for sound levels may differ according to legal rules in the countries.
Therefore, silent mode can only be changed in the service menu.
Please contact your installer/service company to set the silent mode correctly according to your VRF system design.