## Slide 1: Operation modes at VRF air conditioning systems
Product Information

## Slide 2: Several Operation Modes
VRF air conditioning systems
VIP priority
Voting priorities
Capacity vote priority
10 different operation modes gives freedom of usage to end-users
Heating priority
Cooling priority
Cooling only
Heating only
First on priority
Auto priority
Changeover

## Slide 3: Auto Priority Mode (Default)
VRF air conditioning systems
In this mode, outdoor unit will operate in heating priority mode or cooling priority mode according to the outdoor ambient temperature. Mode switching temperature is A, and A can be set by menu [n2-9-0/1/2]
When the outdoor ambient temperature is below (A-3) °C, outdoor units run in heating priority mode. The heating priority mode does not change until the outdoor ambient temperature is above A °C.
When the outdoor ambient temperature is above A °C, the outdoor units run in cooling priority mode. The cooling priority mode does not change until the outdoor ambient temperature is below (A-3) °C.
When the outdoor units restart at outdoor ambient between (A-3) °C and A °C, the outdoor units run the same priority as before the last stop.
When the outdoor unit is initial startup at outdoor ambient temperature between (A-3) °C and A °C, the outdoor units run in heating priority mode.
Priority modes can only be set on the master outdoor unit.
When an indoor unit is in mode conflict with the outdoor units, the unit displays the mode conflict error. The display on indoor unit main PCB will display error code E0.
Settings here is given for AF5301 systems and may differ for other product families.

## Slide 4: Cooling priority mode
VRF air conditioning systems
A) During heating operation:
If an indoor unit requests cooling, the outdoor units stop and then restart in cooling mode after 5 minutes.
Indoor units requesting cooling then start in cooling mode and indoor units requesting heating will display the mode conflict error.
B) During cooling operation:
If an indoor unit requests heating, the outdoor units ignore the request and continue to run in cooling mode.
Indoor units requesting heating displays the mode conflict error.
If all the indoor units requesting cooling are later turned off and one or more indoor units are still requesting heating, the outdoor units restart in heating mode after 5 minutes and any indoor units requesting heating then start in heating mode.
Priority modes can only be set on the master outdoor unit.
When an indoor unit is in mode conflict with the outdoor units, the unit displays the mode conflict error. The display on indoor unit main PCB will display error code E0.
Settings here is given for AF5301 systems and may differ for other product families.

## Slide 5: Heating priority mode
VRF air conditioning systems
A) During cooling operation:
If an indoor unit requests heating, the outdoor units stop and then restart in Heating mode after 5 minutes.
Indoor units requesting heating then start in heating mode and indoor units requesting cooling will display the mode conflict error.
B)During heating operation:
If an indoor unit requests cooling, the outdoor units ignore the request and continue to run in heating mode.
The indoor unit requesting cooling displays the mode conflict error.
If all the indoor units requesting heating are later turned off and one or more indoor units are still requesting cooling, the outdoor units restart in cooling mode after 5 minutes and any indoor unit requesting cooling then starts in cooling mode.
Priority modes can only be set on the master outdoor unit.
When an indoor unit is in mode conflict with the outdoor units, the unit displays the mode conflict error. The display on indoor unit main PCB will display error code E0.
Settings here is given for AF5301 systems and may differ for other product families.

## Slide 6: Cooling Only Mode
VRF air conditioning systems
The outdoor unit(s) only run in cooling mode.
Indoor units requesting cooling, runs in cooling mode
Indoor units requesting heating will display the mode conflict error.
Indoor units in fan only mode, will operate in fan only mode.
Cooling only
Heating Only Mode
Heating only
Priority modes can only be set on the master outdoor unit.
When an indoor unit is in mode conflict with the outdoor units, the unit displays the mode conflict error. The display on indoor unit main PCB will display error code E0.
Settings here is given for AF5301 systems and may differ for other product families.
The outdoor unit(s) only run in heating mode.
Indoor units requesting heating, runs in heating mode.
Indoor units requesting heating will display the mode conflict error.
Indoor units in fan only mode, will display the mode conflict error.

## Slide 7: VIP priority mode
VRF air conditioning systems
The default VIP address is 63.
VIP address also can be changed through menu mode “n1-6”.
In VIP priority mode, if the VIP indoor unit is operating, the outdoor units will operate in the mode of the VIP indoor unit.
In the mean time indoor units, which are in a mode different to that of the VIP unit, will display the mode conflict error (E0).
VIP priority
Priority modes can only be set on the master outdoor unit.
When an indoor unit is in mode conflict with the outdoor units, the unit displays the mode conflict error. The display on indoor unit main PCB will display error code E0.
Settings here is given for AF5301 systems and may differ for other product families.

## Slide 8: Changeover Mode
VRF air conditioning systems
Before using this mode, you need to set the VIP indoor unit address.
The default VIP address is 63 and this address also can be changed through menu mode“n1-6”.
In changeover mode, if the VIP indoor unit is operating, the outdoor units will operate in the mode of the VIP indoor unit.
The other units in the system will follow the mode of the VIP indoor unit, so there will be no mode conflict.
In the changeover mode, the VIP indoor unit can select the auto mode, so that the system can run the auto mode and other indoor unit can follow the VIP indoor unit without mode conflict.
Priority modes can only be set on the master outdoor unit.
When an indoor unit is in mode conflict with the outdoor units, the unit displays the mode conflict error. The display on indoor unit main PCB will display error code E0.
Settings here is given for AF5301 systems and may differ for other product families.

## Slide 9: Voting Priority Modes
VRF air conditioning systems
Voting Priority:
In this mode, outdoor unit operates at heating or cooling mode, depending on the quantity of indoor units which asks for heating or cooling at most.
Capacity Priority:
In this mode, outdoor unit operates at heating or cooling mode, depending on the total capacity of indoor units which asks for heating or cooling at most.
Priority modes can only be set on the master outdoor unit.
When an indoor unit is in mode conflict with the outdoor units, the unit displays the mode conflict error. The display on indoor unit main PCB will display error code E0.
Settings here is given for AF5301 systems and may differ for other product families.

## Slide 10: First On Priority
VRF air conditioning systems
In this mode, the outdoor unit will operate in the mode of the indoor unit which is turned on at first for cooling or Heating.
First on priority
Priority modes can only be set on the master outdoor unit.
When an indoor unit is in mode conflict with the outdoor units, the unit displays the mode conflict error. The display on indoor unit main PCB will display error code E0.
Settings here is given for AF5301 systems and may differ for other product families.