## Slide 1: SEA REGION PARTNER Training TOPIC: AIR-FLUX AF5300 INSTALLATION & COMMISSIONING 08.09.2022 Manisa

## Slide 2: Agenda
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Installation
Commissioning

## Slide 3: Agenda
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Installation
  Refrigerant piping design
  Installation material
  Installation main tools
  Indoor unit installation
  Outdoor unit installation
  Piping installation
  Electrical wiring
  Field settings

## Slide 4: Installation flowchart
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.

## Slide 5: Agenda
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Installation
  Refrigerant piping design
  Installation material
  Installation main tools
  Indoor unit installation
  Outdoor unit installation
  Piping installation
  Electrical wiring
  Field settings

## Slide 6: Refrigerant piping design
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Permitted piping length and drop height
Lc
Lb
La
LA
L1
L6
L2
L7
L8
L9
f
g
h
i
j
L3
L4
L5
a
b
c
d
e
Total piping length |  | ≤ 1000m | L1 + 2 x Ʃ{L2 to L9} + Ʃ{a to j}
Longest length | Actual | ≤ 175m | L1 + Ʃ{L2 to L5} + e
 | Equivalent | ≤ 200m | 
Longest length after first branch |  | ≤ 40m / 90m | Ʃ{L2 to L5} + e
Largest level difference between indoor and outdoor unit | ODU up | ≤ 90m | 
 | ODU down | ≤ 110m | 
Largest level difference between indoor units |  | ≤ 30m | 

## Slide 7
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
The actual longest piping length ≤ 175m
Lc
Lb
La
LA
L1
L6
L2
L7
L8
L9
f
g
h
i
j
L3
L4
L5
a
b
c
d
e
L1+L2+L3+L4+L5+e ≤ 175 m
Note: the equivalent length of each branch joint is 0.5m.
Refrigerant piping design

## Slide 8
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Longest length after first branch ≤ 40/90m
Lc
Lb
La
LA
L1
L6
L2
L7
L8
L9
f
g
h
i
j
L3
L4
L5
a
b
c
d
e
Longest length after first branch should not exceed 40m in length unless the following conditions are met, in which case the permitted length is up to 90m:
a to j ≤ 20m;
(Ʃ{L2 to L5} + e)-(L6 + f) ≤ 40m (the difference in length between the first indoor branch joint to the farthest IDU and to the nearest IDU ;
L2 to L9 diameter increase one size.
Refrigerant piping design

## Slide 9: Agenda
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Installation
  Refrigerant piping design
  Installation material
  Installation main tools
  Indoor unit installation
  Outdoor unit installation
  Piping installation
  Electrical wiring
  Field settings

## Slide 10: Installation material
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Copper Piping storage
If pipes will be used soon, nozzle should be sealed by plastic bag or tape.
If pipes will be stored for a long time, the pipes should be charged with 0.2~0.5MPa Nitrogen and the nozzle should be sealed by welding.

## Slide 11
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Pipe size (mm) | Φ6.35 | Φ9.53 | Φ12.7 | Φ15.9 | Φ19.1 | Φ22.2 | Φ25.4
Thickness (mm) | 0.8 | 0.8 | 0.8 | 1 | 1 | 1 | 1.2
Pipe size (mm) | Φ28.6 | Φ31.8 | Φ34.9 | Φ38.1 | Φ41.3 | Φ44.5 | Φ47.6
Thickness (mm) | 1.2 | 1.2 | 1.2 | 1.5 | 1.5 | 1.5 | 1.5
Remark: Max working pressure of refrigerant is 4.2 MPa (42 bar).

## Slide 12: Installation material
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
The insulating material should be a suitable thickness and the inner diameter should match the size of refrigerant pipes
Insulation material
Pipe diameter | Thickness
Φ6.35~15.9mm | ≥15mm
Φ15.9~38.1mm | ≥20mm
Φ38.1~54.1mm | ≥25mm

## Slide 13: Installation material
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
The branch pipes must be supplied by Midea, otherwise will cause the unbalance of refrigerant distribution, which will reduce the system reliability.
Branch joints
Outdoor branch joints
Indoor branch joints

## Slide 14: Agenda
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Installation
  Refrigerant piping design
  Installation material
  Installation main tools
  Indoor unit installation
  Outdoor unit installation
  Piping installation
  Electrical wiring
  Field settings

## Slide 15: Main tools
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Name | Appearance |  | Name | Appearance
Copper pipe cutter |  |  | Expander | 
Copper pipe bender |  |  | Pressure gauge | 
Flaring tool |  |  | Vacuum pump | 

## Slide 16: Main tools
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Name | Appearance |  | Name | Appearance
Anemometer |  |  | Clamp meter | 
Acoustimeter |  |  | Electric drill | 
Infrared thermometer |  |  |  | 

## Slide 17: Agenda
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Installation
  Refrigerant piping design
  Installation material
  Installation main tools
  Indoor unit installation
  Outdoor unit installation
  Piping installation
  Electrical wiring
  Field settings

## Slide 18: Indoor unit installation
Supports must be strong enough. The supports should be full thread hooks, and their diameters should be ≥ 10mm.
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Hoisting
Full thread hooks
4 Supports for indoor unit

## Slide 19: Indoor unit installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Hoisting
Dual nuts
Single nut

## Slide 20: Indoor unit installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Hoisting
Level meter

## Slide 21: Indoor unit installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Pack the indoor unit with plastic bag after hoisting to protect them from dust entering.
Hoisting

## Slide 22: Indoor unit installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Hoisting
Typical mistakes.
Air outlet too close to wall.
Full thread hooks not vertical.

## Slide 23: Indoor unit installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Hoisting
Typical mistakes.
Improper duct connection.
Air outlet too small.

## Slide 24: Indoor unit installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Access hole for easy maintenance and service
Access hole
No access hole.

## Slide 25: Agenda
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Installation
  Refrigerant piping design
  Installation material
  Installation main tools
  Indoor unit installation
  Outdoor unit installation
  Piping installation
  Electrical wiring
  Field settings

## Slide 26: Outdoor unit installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Installation space requirements
For single unit installation
For single row installation
For multi-row installation

## Slide 27: Outdoor unit installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Installation space requirements
Depending on the height of adjacent walls relative to the height of the units, ducting may be required to ensure proper air discharge. In the situation depicted in below figure, the vertical section of ducting should be at least H-h high.

## Slide 28: Outdoor unit installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Wrong Examples;

## Slide 29: Outdoor unit installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Master and slave unit positioning
In systems with multiple outdoor units, the units should be placed in order from largest capacity unit to smallest capacity unit. The largest capacity unit must be placed on the first branch, and be set as the master unit, while the others should be set as slave units.
All the outdoor units in one combination should be on the same level.

## Slide 30: Outdoor unit installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Base structures
Bases should be constructed on solid ground or on structures of sufficient strength to support the units’ weight.
Bases should be at least 200mm high to provide sufficient access for installation of piping.
Either steel or concrete bases may be suitable.
bases should be completely level.
A drainage ditch should be provided to allow drainage of condensate.

## Slide 31: Outdoor unit installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Base structures
Rubber anti-vibration pads are necessary to avoid vibration.
Rubber Pads

## Slide 32: Outdoor unit installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Protection
Do not remove the package before commissioning

## Slide 33: Agenda
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Installation
  Refrigerant piping design
  Installation material
  Installation main tools
  Indoor unit installation
  Outdoor unit installation
  Piping installation
  Electrical wiring
  Field settings

## Slide 34: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Pipe cutting
Measure the exact length of pipes.
Use the pipe cutter to cut the pipes.
Use scraper to remove the copper burrs.

## Slide 35: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Pipe insulation
Caution: After finishing gastight test, the insulation work should be done on the pipe connection parts and branch pipes.
Purpose
Prevent condensate water adhere to the gas pipe
Protect people from hurt of high temperature
Avoid energy loss

## Slide 36: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Pipe insulation
Block the nozzle of the pipe when make it through the insulation material.
Wrong
Avoid the dust entering the pipe

## Slide 37: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Pipe insulation
The gap between two parts should be well insulated by additional insulation material.
Wrong
Insulation
Right

## Slide 38: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Pipe insulation
The gap between two parts should be well insulated by additional insulation material.

## Slide 39: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Pipe insulation
The insulation work must be done on every part of the refrigerant pipes.

## Slide 40: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Pipe hanging
The distance between the supports of the copper pipes.
Diameter (mm) | ≤20 | 20~40 | ≥40
Distance (m) | 1 | 1.5 | 2
When the liquid pipe and gas pipe are hung up together, it is determined by the diameter of liquid pipe.
Record the actual liquid pipe length for future reference when charging additional refrigerant.

## Slide 41: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Pipe hanging (wrong examples)

## Slide 42: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Pipe connection
U-shaped branch of outdoor side must be installed horizontally.
The branch joint of indoor side can be installed horizontally or vertically.

## Slide 43: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Pipe connection
To avoid accumulation of oil in the outdoor units, outdoor branch joints should be installed horizontally and must not be higher than the outdoor unit refrigerant outlets.

## Slide 44: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Pipe connection

## Slide 45: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Pipe connection
Horizontal branch joints must be installed at an angle to the horizontal not exceeding 10o in order to avoid uneven distribution of refrigerant and possible malfunction.

## Slide 46: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Pipe connection
To ensure even distribution of refrigerant, branch joints should be installed:
More than 500mm of a 90o bend to an branch joint;
More than 500mm of an branch joint to another branch joint;
More than 500mm of the straight section of piping leading to an indoor units;
500 or more
500 or more
500 or more
500 or more
500 or more
Indoor unit
Indoor unit
Indoor unit

## Slide 47: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Pipe connection
Refrigerant flow through bend of branch will cause Turbulent flow, turbulent flow may cause noise and make unbalance refrigerant distribution if not enough distance is satisfied
＞500mm

## Slide 48: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Pipe connection
Sharp bend is too close to branch joint
Two branch joints are too close

## Slide 49: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Pipe connection
Refrigerant piping connection method.
Item | Gas pipe | Liquid pipe
Outdoor unit | Welding | Welding
Indoor unit | Flaring nut | Flaring nut
Branch joint | Welding | Welding

## Slide 50: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Welding
Never flow oxygen through piping as doing so aids oxidation and could easily lead to explosion and as such is extremely dangerous.

## Slide 51: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Welding
Use a pressure reducing valve to flow nitrogen through copper piping at 0.02-0.03MPa during welding.
Start the flow before brazing starts and ensure that the nitrogen continuously passes through the section being welded until the welding is complete and the copper has cooled down completely.
Legend | 
1 | Copper piping
2 | Section being brazed
3 | Nitrogen connection
4 | Hand valve
5 | Pressure-reducing valve
6 | Nitrogen

## Slide 52: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Welding
Why the Nitrogen is necessary?
High temp.
Copper oxide
Hard to be removed clearly
Damage the compressor
Jam the refrigerant system

## Slide 53: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Flushing
Purpose: to remove dust, other particles and moisture, which could cause compressor malfunction.
Flushing should be performed once the piping connections have been completed with the exception of the final connections to the indoor units.
Only use nitrogen for flushing.
Do not connect to indoor units

## Slide 54: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Flushing
The liquid and gas sides can be flushed simultaneously; alternatively, one side can be flushed first and then for the other side.
Use blind plugs to block all liquid (gas) side openings, except for the opening at the indoor unit which is farthest from the outdoor units .
Flush the pipe with 0.5 MPa Nitrogen.
Use your hand to block the opening, when the pressure is too high to block, then remove your hand.
Repeat the step 3 until on further dirt or moisture is emitted from the piping. Seal the opening once it has been flushed.
Flushing the other openings in the same manner, working in sequence from the farthest indoor unit towards the outdoor unit.
After flushing, seal all the openings.
Pipe flushing sequence (1-2-3-4-5-6 working towards the ODU)

## Slide 55: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Flushing

## Slide 56: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Gastightness test
Purpose: to prevent faults caused by refrigerant leakage, a gastightness test should be performed before system commission.
Only dry nitrogen should be used for gastightness testing.
Keep the liquid and gas stop valves fully closed.
The piping system is complete and the indoor and outdoor units have been connected.
Charge N2 until the gauge shows slowly and orderly through the needle valves on the liquid and gas stop valves
Procedure

## Slide 57: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Gastightness test
1st stage:
Large leakage check: 0.3MPa more than 3 minutes
2nd stage:
Small leakage check: 1.5MPa more than 3 minutes
3rd stage:
Micro leakage check: 4.0MPa more than 24 hours
Check for micro leakages:
If there’s 1oC difference in temperature, there will be 0.01MPa difference in pressure.
Correcting formula:
Actual value = Pressure when finish charging +(current temp. – temp. when finish charging)
x 0.01MPa

## Slide 58: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Gastightness test
Example:
Temp. when charging N2: 24oC
N2 pressure when charging: 3.8MPa
Temp. after 24 hours: 22oC
N2 pressure after 24hours
= 3.8MPa + (22oC-24oC) x 0.01MPa/oC
= 3.8MPa -0.02MPa
= 3.78MPa
If the actual pressure after 24hours is lower than 3.78MPa, you need to check leakage.

## Slide 59: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Vacuum
Purpose: to remove moisture and non-condensable gases from the system.
A vacuum pump capable of maintaining a pressure of -0.1MPa or lower should be used. Using a vacuum pump with a discharge in excess of 4L/s and a precision level of 0.02mmHg is recommended.
Keep the liquid and gas stop valves fully closed.
Connect to the vacuum pump
Vacuum the system till the time when gauge shows -0.1Mpa
When vacuum to -0.1MPa, continue vacuuming for 2h
Stop vacuuming
After 1 hour, check the pressure gauge
Procedure

## Slide 60: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Vacuum
Pressure gauge

## Slide 61: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Charging refrigerant
Only charge refrigerant after performing a gastightness test and vacuum drying.
Never charge more refrigerant than required as doing so can lead to liquid hammering.
Only use refrigerant R410A, use tools and equipment designed for use with R410A.
Always use protective gloves and protect your eyes when charging refrigerant.
Calculate necessary amount of additional refrigerant according to the diameter and length of liquid pipe
Keep the liquid and gas stop valves fully closed, charge refrigerant through gas and liquid stop valves at the same time
When the amount charged reaches R (kg), finish charging
If the amount charged has not reached R (kg) but no additional refrigerant can be charged, open the gas and liquid stop valves, run the outdoor units in cooling mode, and continue charging until the full R (kg) of refrigerant has been charged
Procedure

## Slide 62: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Charging refrigerant
The additional refrigerant charge required depends on the lengths and diameters of the outdoor and indoor liquid pipes.
Assume 0.5m for the equivalent pipe length of each branch joint.
Liquid side piping (mm) | Additional refrigerant charge per meter of equivalent length of piping (kg)
Φ6.35 | 0.022
Φ9.53 | 0.057
Φ12.7 | 0.110
Φ15.9 | 0.170
Φ19.1 | 0.260
Φ22.2 | 0.360
Φ25.4 | 0.520
Φ28.6 | 0.680
Additional refrigerant charge R (kg) =L1(Φ6.35)×0.022+L2(Φ9.53)×0.057+L3(Φ12.7)×0.110+L4(Φ15.9)×0.170+L5(Φ19.1)×0.260+L6 (Φ22.2)×0.360+L7(Φ25.4)×0.520+L8(Φ28.6)×0.680
Where L1 to L8 represent the equivalent lengths of the liquid pipes of different diameters.

## Slide 63: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Drain Piping
Selection steps
Condensate water volume (L/h) =
Indoor unit capacity (HP) × 2L/h
Select the diameter according to the below table
Condensate water volume : V (L/h) | I.D (mm) | Thickness (mm)
V ≤ 14 | Φ 25 | 3.0
14 ＜ V ≤ 88 | Φ 30 | 3.5
88 ＜ V ≤ 175 | Φ 40 | 4.0
175 ＜ V ≤ 334 | Φ 50 | 4.5
334 ＜ V | Φ 80 | 6.0

## Slide 64: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Drain Piping
Caution：
The slope of main drain piping must be bigger than 1%.
If the slope < 1%, then select drain piping with bigger diameter.
The length of drain piping should be as short as possible.
The drain piping should be independent with other water pipe.
Never put the drain piping together with dirty water pipe.

## Slide 65: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Drain Piping
To avoid the bending, recommended support/hanger spacing is 0.8 – 1.0m for horizontal piping and 1.5 – 2.0m for vertical piping.
Each vertical section should be fitted with at least two supports. For horizontal piping, spacing greater than those recommended leads to sagging and deformation of the pipe profile at the supports which impedes water flow and should therefore be avoided.

## Slide 66: Piping installation
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Drain Piping
Air vents should be fitted at the highest point of each drain piping system to ensure that condensation is discharged smoothly.
U-bends or elbow joints should be used such that the vents face downwards, to prevent dust entering the piping.
Air vents should not be installed too close to indoor unit lift pumps.

## Slide 67: Agenda
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Installation
  Refrigerant piping design
  Installation material
  Installation main tools
  Indoor unit installation
  Outdoor unit installation
  Piping installation
  Electrical wiring
  Field settings

## Slide 68: Electrical Wiring
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Power Supply Wiring
Basic requirement
All wiring work must be done by qualified person
All wires, and electric devices must be conformed to local standards
Voltage range: rated voltage ±10%
Independent power supply
Capacity of power device is large enough
Well and reliable PE line

## Slide 69: Electrical Wiring
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Power Supply Wiring
Power supply for outdoor unit
Power supply box
Leakage protector
/Manual switch
3-Phase
380/400/415V

## Slide 70: Electrical Wiring
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Power Supply Wiring
Power supply for indoor unit

## Slide 71: Electrical Wiring
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Power Supply Wiring
For indoor / outdoor unit power wire sizing and circuit breaker sizing, refer to indoor / outdoor unit “Electrical Characteristics”.
Select wire size based on the value of MCA in “Electrical Characteristics”.
Select overcurrent circuit breakers and residual-current circuit breakers based on the value of MFA in “Electrical Characteristics”.

## Slide 72: Electrical Wiring
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Communication Wiring
0.75mm2 3-core shielded cable is recommended for communication wiring. Using other types of cable can lead to interference and malfunction.
In installations where no strong electromagnetic fields are present, 2-core non-polarized shielded communication wiring can be used for indoor and outdoor unit (P Q) communication.

## Slide 73: Electrical Wiring
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Communication Wiring
The P Q E communication wires should be connected one unit after another in a daisy chain from the ODU to the final IDU for indoor and outdoor units communication.
The H1 H2 E communication wires should be connected one unit after another in a daisy chain from the master ODU to the final slave ODU for outdoor units communication.
H1,H2,E
H1,H2,E
H1,H2,E
P,Q,E
Master unit
Slave unit
Slave unit
P,Q,E
P,Q,E
P,Q,E
P,Q,E
NOTE:
At the final indoor unit, a 120Ω resistor should be connected between the P and Q terminals.
The shielding nets of the communication wires should be connected together and grounded.

## Slide 74: Electrical Wiring
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Communication Wiring
Communication wiring configurations – correct and incorrect examples.

## Slide 75: Electrical Wiring
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Communication Wiring
Communication wiring configurations – correct and incorrect examples.

## Slide 76: Electrical Wiring
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Communication Wiring
Communication wiring configurations – correct and incorrect examples.

## Slide 77: Electrical Wiring
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Communication Wiring
The X Y E communication wires should be connected to master unit for indoor units and indoor unit centralized controller communication.
IDU centralized controller
X,Y,E
H1,H2,E
H1,H2,E
H1,H2,E
P,Q,E
Master unit
Slave unit
Slave unit
P,Q,E
P,Q,E
P,Q,E
P,Q,E

## Slide 78: Electrical Wiring
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Communication Wiring
To prevent signal interference, the power wiring and communication wiring should not be run in the same conduit.
If the power supply is less than 10A, a separation of at least 300mm between power wiring and communication wiring conduits should be maintained
If the power supply is in the range 10A to 50A then a separation of at least 500mm should be maintained.

## Slide 79: Agenda
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Installation
  Refrigerant piping design
  Installation material
  Installation main tools
  Indoor unit installation
  Outdoor unit installation
  Piping installation
  Electrical wiring
  Field settings

## Slide 80: Field setting
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
PCB switches and
switch settings

## Slide 81: Field setting
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Switch settings
NOTE:
Black denotes the switch position.

## Slide 82: Field setting
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Switch settings
NOTE:
Black denotes the switch position.

## Slide 83: Field setting
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Switch settings
NOTE:
Black denotes the switch position.

## Slide 84: Field setting
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Switch settings
NOTE:
Black denotes the switch position.

## Slide 85: Field setting
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Switch settings
NOTE:
Black denotes the switch position.
ACC – MT (Central Controller)

## Slide 86: Field setting
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Switch settings
NOTE:
Black denotes the switch position.

## Slide 87: Field setting
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Switch settings
NOTE:
Black denotes the switch position.

## Slide 88: Field setting
Air Flux - Installation and Commissioning
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Switch settings
NOTE:
Black denotes the switch position.

## Slide 89: ODU Sockets Descriptions
Field Settings
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.

## Slide 90: Odu Parameter Settings
Field Settings
1- Rotary Switches
2- Digital Screen DSP2
3- Digital Screen DSP1
4- SW3 - SW6 buttons
5- Dip Switch
6- Main Processor of Board
3
2
1
6
5
4
SW3-SW6 button functions
Display Output
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.

## Slide 91: Odu Parameter Monitoring
Field Settings
Display Screen Parameters
DSP1 | Parameters displayed on DSP2 | Remarks
0 | Unit address | For ODU’s : 0-2
1 | Unit capacity | Values: 0 (8HP); 1 (10HP); 2 (12HP); 3 (14HP); 4 (16HP); 5 (18HP); 6 (20HP); 7 (22HP); 8 (24HP); 9 (26HP); A (28HP); B (30HP); C (32HP)
2 | Number of outdoor units | Only available for master unit.
3 | Number of indoor units as set on PCB | Only available for master unit.
4 | Total capacity of the outdoor units | Only available for master unit. display on slave units makes no sense
5 | Total capacity requirement of the indoor units | Only available for master unit.
6 | Total capacity requirement correction of the master unit | Only available for master unit.
7 | Operating mode | Operation mode: 0 (OFF); 2 (cooling); 3 (heating); 4 (forced cooling)
8 | Actual operating capacity of the outdoor unit | 
9 | Fan A speed index | Range 1 (slowest) --- 35 (fastest)
10 | Fan B speed index | Range 1 (slowest) --- 35 (fastest)
11 | T2/T2B average temperature [ °C] | 
12 | Main heat exchanger pipe (T3) temperature [ °C] | 
13 | Outdoor ambient (T4) temperature [ °C] | 
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.

## Slide 92: Odu Parameter Monitoring
Field Settings
Display Screen Parameters
14 | Plate heat exchanger cooling refrigerant inlet (T6A) temperature [ °C] | 
15 | Plate heat exchanger cooling refrigerant outlet(T6B) temperature [ °C] | 
16 | Discharge temperature of compressor A [ °C] | 
17 | Discharge temperature of compressor B [ °C] | 
18 | Inverter-module heatsink temperature A [ °C] | 
19 | Inverter-module heatsink temperature B [ °C] | 
20 | Plate exchanger degree of superheat [ °C] | 
21 | Discharge superheat degree | 
22 | Inverter compressor A current [A] | 
23 | Inverter compressor B current [A] | 
24 | EEVA position | Opening angle of EEV: Actual value = Display value x 4(480P) or Actual value = Display value x 24(3000P)
25 | EEVB position | Opening angle of EEV: Actual value = Display value x 4(480P) or Actual value = Display value x 24(3000P)
26 | EEVC position | Opening angle of EEV: Actual value = Display value x 4(480P)
27 | Compressor discharge pressure [MPa] | High pressure: Actual value = Display value x 0.1 MPa
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.

## Slide 93: Odu Parameter Monitoring
Field Settings
Display Screen Parameters
29 | Number of indoor units currently in communication with master unit | 
30 | Number of indoor units currently operating | Only available for master unit.
31 | Priority mode | Priority mode: 0 (auto priority); 1 (cooling priority); 2 (VIP priority or voting priority); 3(heating only); 4 (cooling only)
32 | Silent mode | Silent mode: 0 (night silent time is 6h/8h); 1 (night silent time is 6h/12h), 2 (night silenttime is 8h/10h); 3 (night silent time is 8h/12h); 7 (silent mode 3); 8 (super silent mode1); 9 (super silent mode 2); 10 (super silent mode 3); 11 (super silent mode 4)
33 | Static pressure mode | Static pressure mode: 0 (standard static pressure); 1 (low static pressure); 2 (medium static pressure); 3 (high static pressure); 4 (super high static pressure)
36 | DC bus voltage A | DC bus voltage: Actual value = Display value x 10 V
37 | DC bus voltage B | DC bus voltage: Actual value = Display value x 10 V
38 | Reserved | 
39 | Address of VIP indoor unit | 
40 | Reserved | 
41 | Reserved | 
42 | Refrigerant state | Refrigerant quantity: 0 (normal); 1 (slightly excessive); 2 (significantly excessive); 11 (slightly insufficient); 12 (significantly insufficient); 13 (critically insufficient)
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.

## Slide 94: Odu Parameter Monitoring
Field Settings
Display Screen Parameters
44 | Power mode | 00 (100% capacity output); 01 (90% capacity output); 02 (80% capacity output); 03(70% capacity output); 04 (60% capacity output); 05 (50% capacity output); 06 (40%capacity output); 10 (auto power save mode, 100% capacity output); 11 (auto power save mode, 90% capacity output); 12 (auto power save mode, 80% capacity output); 13(auto power save mode 70% capacity output); 14 (auto power save mode, 60% capacityoutput); 15 (auto power save mode, 50% capacity output); 16 (auto power save mode, 40% capacity output)
45 | Most recent error or protection code | 
– | – | End Check
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.

## Slide 95: Odu Parameter Settings
Field Settings
Display Screen Parameters
Menu Details
Only reachable by master ODU unit
Press&hold 5 sec. To SW5 for accessing to ‘Menu’ parameters
n1 will be shown on digital screen. SW3 / SW4 UP / DOWN buttons will direct you to select n1, n2, n3, n4 veya nb parameters. Use SW6 OK button for entering to selected menu
If you select n4, then second digit will be blinking. Use SW3 / SW4 UP / DOWN for selecting paramaters which is between n41 - n47
For example n43 you selected then pushed to SW6 OK button. It means you set limit for ODU unit working capacity
For turning back to previous menü, please push SW5
MENÜ | Açıklama | Not
n14 | Debug mode 1 | Only available for master unit. All indoor units will run in cooling mode.
n15 | Debug mode 2 | Only available for master unit. If all the indoor units in the system are the 2nd heating mode. If there is one or more old indoor units in the system, all the indoor units will run in force cooling mode.
n16 | Maintenance Mode | Only available for the master unit. The system does not check the number of the indoor units.
n26 | Backup run | Only available for outdoor units with two compressors. If one of the two compressors fails, the other compressor runs for up to 4 days and then stops automatically.
n27 | Vacuum mode | Only used for maintenance process. Display shows “R006”. All solenoid valves and EXVs are open at maximum.
n31 | History error codes | Displays the last ten error codes.
n32 | Cleaning history error codes | 
n34 | Restore factory settings | Only available for the master unit.
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.

## Slide 96: Odu Parameter Settings
Field Settings
Display Screen Parameters
MENÜ | Descriptions | Notice
n41 | Power limitation mode 1 | Only available for the master unit, 100% capacity output.
n42 | Power limitation mode 2 | Only available for the master unit, 90% capacity output.
n43 | Power limitation mode 3 | Only available for the master unit, 80% capacity output.
n44 | Power limitation mode 4 | Only available for the master unit, 70% capacity output.
n45 | Power limitation mode 5 | Only available for the master unit, 60% capacity output.
n46 | Power limitation mode 6 | Only available for the master unit, 50% capacity output.
n47 | Power limitation mode 7 | Only available for the master unit, 40% capacity output.
nb1 | Fahrenheit degree ( °F) | Only available for master unit.
nb2 | Celsius degree ( °C) | Only available for master unit.
nb3 | Exit auto energy saving mode | Only available for master unit.
nb4 | Enter auto energy saving mode | Only available for master unit.
nb5 | Auto snowblowing mode 1 | Depends on ODU ambient temp. (T4), fans work 2 min in each 15 min. regularly
nb6 | Auto snowblowing mode 2 | Depends on ODU ambient temp. (T4), fans work 2 min in each 30 min. regularly
nb7 | Exit auto snowblowing mode | 
nb8 | VIP address setting | It shows the VIP address
nc1 | Auto dust-clean mode | 
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.

## Slide 97: Adressing by Remote Controller
Field Settings
Setting & monitoring the address
Push & hold 8 sec to the buttons (left 3 button) which are colored to grey.
Then push on/off button which is shown at fig.2. After that define your address by using up/down button.
Push fan button to set idu address then number will be shown on idu display
For exiting from menu, please use same button which you used for entering the menü (left 3 button)
Fig. 1
Fig. 2
Addressing by Remote Controller
Monitoring the address by Remote Controller
First 2 conditions are same as at above. In 3rd condition use ‘mode’ instead of ‘fan speed’
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.

## Slide 98: Agenda
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Installation
Commissioning

## Slide 99
Pre-commissioning checks
Power / communication wiring
Refrigerant pipe & insulation
Pressure test & vacuum dry
Are the electrical wiring connected?
Are the wiring specifications correct?
Are the power cables well insulated?
Are they all properly connected ? (PQE,XYE and F1F2E)
Additional refrigerant charge
Check valves
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Notes: Labyrinth structure
Frame integrated with the thermal insulation panel through the high-pressure polyurethane foam of the density of 50kg/m3.
Connection between panels enabled by tenon structure
Inside steel frame with double side reinforcements at each joint (as illustrated in the figure), provide a good solution for unit rigidity.

## Slide 100
Pre-commissioning checks
Power / communication wiring
Refrigerant pipe & insulation
Pressure test & vacuum dry
Are the pipe diameters correct?
Are all pipes well insulated?
Additional refrigerant charge
Check valves
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Notes: Labyrinth structure
Frame integrated with the thermal insulation panel through the high-pressure polyurethane foam of the density of 50kg/m3.
Connection between panels enabled by tenon structure
Inside steel frame with double side reinforcements at each joint (as illustrated in the figure), provide a good solution for unit rigidity.

## Slide 101
Pre-commissioning checks
Power / communication wiring
Refrigerant pipe & insulation
Pressure test & vacuum dry
Has the pressure test been inspected & achieved?
Has the vacuum dry been carried out and reached -0.1MPa?
Additional refrigerant charge
Check valves
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Notes: Labyrinth structure
Frame integrated with the thermal insulation panel through the high-pressure polyurethane foam of the density of 50kg/m3.
Connection between panels enabled by tenon structure
Inside steel frame with double side reinforcements at each joint (as illustrated in the figure), provide a good solution for unit rigidity.

## Slide 102
Pre-commissioning checks
Power / communication wiring
Refrigerant pipe & insulation
Pressure test & vacuum dry
Has the refrigerant been charged correctly?
Additional refrigerant charge
Check valves
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Notes: Labyrinth structure
Frame integrated with the thermal insulation panel through the high-pressure polyurethane foam of the density of 50kg/m3.
Connection between panels enabled by tenon structure
Inside steel frame with double side reinforcements at each joint (as illustrated in the figure), provide a good solution for unit rigidity.

## Slide 103
Pre-commissioning checks
Check valves
Preheat
Standby mode
Are all outdoor valves open?
Operation test
Hand to user
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Notes: Labyrinth structure
Frame integrated with the thermal insulation panel through the high-pressure polyurethane foam of the density of 50kg/m3.
Connection between panels enabled by tenon structure
Inside steel frame with double side reinforcements at each joint (as illustrated in the figure), provide a good solution for unit rigidity.

## Slide 104
Pre-commissioning checks
Check valves
Preheat
Standby mode
Are all outdoor units powered on 24hours before start?
Operation test
Hand to user
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Notes: Labyrinth structure
Frame integrated with the thermal insulation panel through the high-pressure polyurethane foam of the density of 50kg/m3.
Connection between panels enabled by tenon structure
Inside steel frame with double side reinforcements at each joint (as illustrated in the figure), provide a good solution for unit rigidity.

## Slide 105
Pre-commissioning checks
Check valves
Preheat
Standby mode
Power on all indoor units.
Check if there are any error codes displayed on the PCB’s of the IDU or ODU?
Check whether the ODU LED displays the actual quantity of all IDU’s?
Operation test
Hand to user
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Notes: Labyrinth structure
Frame integrated with the thermal insulation panel through the high-pressure polyurethane foam of the density of 50kg/m3.
Connection between panels enabled by tenon structure
Inside steel frame with double side reinforcements at each joint (as illustrated in the figure), provide a good solution for unit rigidity.

## Slide 106
Commissioning trial runs
Check valves
Preheat
Standby mode
Test run procedure:
Run in cooling mode
Setting temp. 17oC
High fan speed
After 1 hour, check the system parameters through UP/DOWN button
Run in heating mode
Setting temp. 30oC
High fan speed
After 1 hour, check the system parameters through UP/DOWN button
Operation test
Hand to user
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Notes: Labyrinth structure
Frame integrated with the thermal insulation panel through the high-pressure polyurethane foam of the density of 50kg/m3.
Connection between panels enabled by tenon structure
Inside steel frame with double side reinforcements at each joint (as illustrated in the figure), provide a good solution for unit rigidity.

## Slide 107
Commissioning trial runs
Normal operating parameters of refrigerant system
Outdoor ambient temp. | °C | < 10 | 10 to 26 | 26 to 31 | 31 to 41 | > 41
Average discharge temp. | °C | 60-76 | 62-78 | 65-82 | 67-92 | 69-92
Average discharge superheat | °C | 17-30 | 17-33 | 17-34 | 17-36 | 10-32
Discharge pressure | MPa | 2.3-2.8 | 2.3-2.8 | 2.4-3.6 | 2.6-3.8 | 3.1-4.2
Suction pressure | MPa | 0.6-0.7 | 0.7-0.9 | 0.8-1.0 | 1.0-1.2 | 1.2-1.4
DC inverter compressor current | A | 9-20 | 11-22 | 12-25 | 15-29 | 20-26
Cooling:
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Notes: Labyrinth structure
Frame integrated with the thermal insulation panel through the high-pressure polyurethane foam of the density of 50kg/m3.
Connection between panels enabled by tenon structure
Inside steel frame with double side reinforcements at each joint (as illustrated in the figure), provide a good solution for unit rigidity.

## Slide 108
Commissioning trial runs
Normal operating parameters of refrigerant system
Heating:
Outdoor ambient temp. | °C | < -10 | -10 to 0 | 0 to 5 | 5 to 10 | 10 to 17 | > 17
Average discharge temp. | °C | 56-74 | 57-76 | 58-78 | 61-82 | 63-82 | 63-82
Average discharge superheat | °C | 17-35 | 17-35 | 17-35 | 17-33 | 14-33 | 14-33
Discharge pressure | MPa | 1.7-2.4 | 1.8-2.5 | 1.9-3.0 | 2.2-3.2 | 2.3-3.2 | 2.3-3.2
Suction pressure | MPa | 1.4-1.6 | 1.5-1.7 | 1.6-2.2 | 1.8-2.6 | 1.8-2.6 | 2.0-2.4
DC inverter compressor current | A | 11-25 | 13-27 | 12-28 | 11-28 | 11-25 | 15-20
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Notes: Labyrinth structure
Frame integrated with the thermal insulation panel through the high-pressure polyurethane foam of the density of 50kg/m3.
Connection between panels enabled by tenon structure
Inside steel frame with double side reinforcements at each joint (as illustrated in the figure), provide a good solution for unit rigidity.

## Slide 109
Hand over
Check valves
Preheat
Standby mode
Full commissioning sheets
Engineering data book
Service manual
Operation test
Hand to user
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Notes: Labyrinth structure
Frame integrated with the thermal insulation panel through the high-pressure polyurethane foam of the density of 50kg/m3.
Connection between panels enabled by tenon structure
Inside steel frame with double side reinforcements at each joint (as illustrated in the figure), provide a good solution for unit rigidity.

## Slide 110
Hand over
Full commissioning sheets
Engineering data book
Service manual
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Notes: Labyrinth structure
Frame integrated with the thermal insulation panel through the high-pressure polyurethane foam of the density of 50kg/m3.
Connection between panels enabled by tenon structure
Inside steel frame with double side reinforcements at each joint (as illustrated in the figure), provide a good solution for unit rigidity.

## Slide 111
Thank you for attendance
© Bosch Thermotechnik GmbH 2018. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Notes: Labyrinth structure
Frame integrated with the thermal insulation panel through the high-pressure polyurethane foam of the density of 50kg/m3.
Connection between panels enabled by tenon structure
Inside steel frame with double side reinforcements at each joint (as illustrated in the figure), provide a good solution for unit rigidity.