## Slide 1: SEA REGION PARTNER Training TOPIC: AIR-FLUX product Features 08.09.2022 Manisa

## Slide 2
09:00 - 09:45 VRF ODU Product Line-Up
09:45 - 10:30 VRF IDU Product Line-Up
10:30 - 10:45 Break
10:45 - 12:15 Product Features of AF5300 (2 pipe system)
12:15 - 13:15 Lunch Break
13:15 - 14:00 Product Features of AF6300 (3 pipe system)
14:00 – 14:45 Product Features of Ahu kit & Hydrobox & ERV units (3 pipe system)
14:45 - 15:00 Break
15:00 - 16:30 Controllers & Gateway
16:30 - 16:45 Q & A
09:00 - 10:30 VRF Installation
10:30 - 10:45 Break
10:45 – 11:30 VRF Commissioning Theoratical
11:30 - 12:15 VRF Commissioning Practical
12:15 - 13:15 Lunch Break
13:15 - 14:00 Electrical Circuit and Components
14:00 - 14:45 Refrigerant Circuit and Components
14:45 - 15:00 Break
15:00 - 15:15 Defrost & Oil Return & Start-Up Trouble Shooting
15:15 - 16:45 Trouble Shooting
16:45 - 17:00 Q & A
20.10.2022 Thursday
19.10.2022 Wednesday

## Slide 3
09:00 - 09:45 VRF ODU Product Line-Up
09:45 - 10:30 VRF IDU Product Line-Up
10:45 – 11:00 Break
10:45 - 11:30 Product Features of AF5300 (2 pipe system)
11:30 - 12:15 Product Features of AF6300 (3 pipe system)
12:15 - 13:15 Lunch Break
13:15 - 14:00 Product Features of Ahu kit & Hydrobox (3 pipe system)
14:00 - 14:45 Controllers & Gateway
14:45 - 15:00 Break
15:00 - 16:45 VRF installations
16:45 - 17:00 Q & A
VRF Commissioning
16:45 - 17:00 Q&A session
17:00 - 19:00 Field Visit (Include Travel Time)

## Slide 4: Product Line up & Feature
Af5300 ODU ( 2 Pipe)
AF6300 ODU ( 3 Pipe)
Ahu-Kit D
HydroBox
ERV unit
Controllers

## Slide 5: Product Line up & Feature
AF5300 ODU
13 different models with a capacity up to 90 kW
Free modular combination with 2HP increase up to 270 kW
Combination ratio min %50 ~ max %130
CE and Eurovent certified
HP | 8  12 | 14 - 16 | 18  22 | 24  32
kW | 25  33,5 | 40 - 45 | 50  62 | 67  90
HP | 32  64 |  | 64  96 | 
kW | 90  180 |  | 180  270 | 
- 2250 m2 area can be air-conditioned with one system.
*Cooling load estimated as 120W/m2

## Slide 6: Connectable Max. IDU Quantity
AF5300 ODU
Product Type | Rated Cooling Capacity |  | Maximum number of connected indoor units
 | kW | HP | 
AF5300A 25 C-3 | 25.2 | 8 | 13
AF5300A 28 C-3 | 28.0 | 10 | 16
AF5300A 33 C-3 | 33.5 | 12 | 20
AF5300A 40 C-3 | 40.0 | 14 | 23
AF5300A 45 C-3 | 45.0 | 16 | 26
AF5300A 50 C-3 | 50.0 | 18 | 29
AF5300A 56 C-3 | 56.0 | 20 | 33
AF5300A 62 C-3 | 61.5 | 22 | 36
AF5300A 67 C-3 | 67.0 | 24 | 39
AF5300A 73 C-3 | 73.0 | 26 | 43
AF5300A 79 C-3 | 78.5 | 28 | 46
AF5300A 85 C-3 | 85.0 | 30 | 50
AF5300A 90 C-3 | 90.0 | 32 | 53
AF5300A 95 C-3 | 95.0 | 34 | 56
AF5300A 102 C-3 | 101.5 | 36 | 59
AF5300A 107 C-3 | 106.5 | 38 | 63
AF5300A 112 C-3 ~ AF5300A 270 C-3 | 112  270 | 40  96 | 64

## Slide 7: Combination Range
AF5300 ODU
System capacity |  | Number of units | Modules1 |  |  |  |  |  |  |  |  |  |  |  |  | Outdoor branch joint kit2
kW | HP |  | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26 | 28 | 30 | 32 | 
95.0 | 34 | 2 |  |  | ● |  |  |  |  | ● |  |  |  |  |  | AF-BJO 02
101.5 | 36 | 2 |  |  |  | ● |  |  |  | ● |  |  |  |  |  | 
106.5 | 38 | 2 |  |  |  |  | ● |  |  | ● |  |  |  |  |  | 
112.0 | 40 | 2 |  |  | ● |  |  |  |  |  |  |  | ● |  |  | 
117.5 | 42 | 2 |  |  |  |  |  |  | ● | ● |  |  |  |  |  | 
123.0 | 44 | 2 |  |  |  |  |  |  |  | ●● |  |  |  |  |  | 
128.5 | 46 | 2 |  |  |  |  |  |  |  | ● | ● |  |  |  |  | 
134.5 | 48 | 2 |  |  |  |  |  |  |  | ● |  | ● |  |  |  | 
140.0 | 50 | 2 |  |  |  |  |  |  |  | ● |  |  | ● |  |  | 
146.0 | 52 | 2 |  |  |  |  |  |  |  |  |  | ●● |  |  |  | 
151.5 | 54 | 2 |  |  |  |  |  |  |  |  |  | ● | ● |  |  | 
157.0 | 56 | 2 |  |  |  |  |  |  |  |  |  |  | ●● |  |  | 
163.5 | 58 | 2 |  |  |  |  |  |  |  |  |  |  | ● | ● |  | 
168.5 | 60 | 2 |  |  |  |  |  |  |  |  |  |  | ● |  | ● | 
175.0 | 62 | 2 |  |  |  |  |  |  |  |  |  |  |  | ● | ● | 
180.0 | 64 | 2 |  |  |  |  |  |  |  |  |  |  |  |  | ●● | 
185.0 | 66 | 3 |  |  | ● |  |  |  |  | ● |  |  |  |  | ● | AF-BJO 03
191.5 | 68 | 3 |  |  |  | ● |  |  |  | ● |  |  |  |  | ● | 
196.5 | 70 | 3 |  |  |  |  | ● |  |  | ● |  |  |  |  | ● | 
202.0 | 72 | 3 |  |  | ● |  |  |  |  |  |  |  | ● |  | ● | 
207.5 | 74 | 3 |  |  |  |  |  |  | ● | ● |  |  |  |  | ● | 
213.0 | 76 | 3 |  |  |  |  |  |  |  | ●● |  |  |  |  | ● | 
218.5 | 78 | 3 |  |  |  |  |  |  |  | ● | ● |  |  |  | ● | 
224.5 | 80 | 3 |  |  |  |  |  |  |  | ● |  | ● |  |  | ● | 
230.0 | 82 | 3 |  |  |  |  |  |  |  | ● |  |  | ● |  | ● | 
236.0 | 84 | 3 |  |  |  |  |  |  |  |  |  | ●● |  |  | ● | 
241.5 | 86 | 3 |  |  |  |  |  |  |  |  |  | ● | ● |  | ● | 
247.0 | 88 | 3 |  |  |  |  |  |  |  |  |  |  | ●● |  | ● | 
253.5 | 90 | 3 |  |  |  |  |  |  |  |  |  |  | ● | ● | ● | 
258.5 | 92 | 3 |  |  |  |  |  |  |  |  |  |  | ● |  | ●● | 
265.0 | 94 | 3 |  |  |  |  |  |  |  |  |  |  |  | ● | ●● | 
270.0 | 96 | 3 |  |  |  |  |  |  |  |  |  |  |  |  | ●●● | 
Notes: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
1. The combinations of units shown in the table are factory-recommended. Other combinations of units are also possible. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
2. For systems with two or more outdoor units, outdoor branch joints (sold separately) are required. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
At beside there is suggested combination table for ODU‘s.
According to customer requirement and project design , it can be changed flexibly

## Slide 8: Energy Specifications
Model | Power Supply1 |  |  |  |  |  |  | Compressor |  | OFM | 
Product Type | Hz | Voltage | Min. voltage | Max. voltage | MCA2 | TOCA3 | MFA4 | MSC5 | RLA6 | kW | FLA
AF5300A 25 C-3 | 50/60 | 380~415 | 342 | 440 | 24.0 | 30.9 | 32 | / | 10 | 0.56 | 6.3
AF5300A 28 C-3 | 50/60 | 380~415 | 342 | 440 | 25.2 | 30.9 | 32 | / | 10.6 | 0.56 | 6.3
AF5300A 33 C-3 | 50/60 | 380~415 | 342 | 440 | 26.4 | 31.5 | 32 | / | 15.4 | 0.56 | 6.9
AF5300A 40 C-3 | 50/60 | 380~415 | 342 | 440 | 33.1 | 40.3 | 40 | / | 25.8 | 0.92 | 7.3
AF5300A 45 C-3 | 50/60 | 380~415 | 342 | 440 | 33.1 | 40.3 | 40 | / | 25.8 | 0.92 | 7.3
AF5300A 50 C-3 | 50/60 | 380~415 | 342 | 440 | 40.8 | 59.3 | 50 | / | 14+13 | 0.56×2 | 10.1
AF5300A 56 C-3 | 50/60 | 380~415 | 342 | 440 | 43.9 | 60.1 | 50 | / | 17+16 | 0.56×2 | 10.9
AF5300A 62 C-3 | 50/60 | 380~415 | 342 | 440 | 47.9 | 60.1 | 63 | / | 19+18 | 0.56×2 | 10.9
AF5300A 67 C-3 | 50/60 | 380~415 | 342 | 440 | 48.4 | 62.3 | 63 | / | 17.4+16.6 | 0.92×2 | 13.1
AF5300A 73 C-3 | 50/60 | 380~415 | 342 | 440 | 52.9 | 62.3 | 63 | / | 20+19.8 | 0.92×2 | 13.1
AF5300A 79 C-3 | 50/60 | 380~415 | 342 | 440 | 58.7 | 64.1 | 63 | / | 22+21.8 | 0.92×2 | 14.9
AF5300A 85 C-3 | 50/60 | 380~415 | 342 | 440 | 64.9 | 72.5 | 80 | / | 20+30 | 0.92×2 | 14.9
AF5300A 90 C-3 | 50/60 | 380~415 | 342 | 440 | 66.9 | 72.5 | 80 | / | 22+30 | 0.92×2 | 14.9
Abbreviations:
MCA : Minimum Circuit Amps
TOCA : Total Over-current Amps
MFA : Maximum Fuse Amps
MSC : Maximum Starting Current (A)
RLA : Rated Load Amps
FLA : Full Load Amps
OFM : Outdoor unit fan motor
AF5300
MCA (Minimum Circuit Ampacity)
It is used for conductor sizing to ensure that the wiring does not overheat under normal operating conditions. . The minimum circuit ampacity (MCA) is the minimum wire size required for a field wired product. It is chosen to guarantee that the wiring will not overheat under the expected operating conditions.
MFA (Maximum Fuse Amps)
This value is required for the protection of motor (fan motor), given by manufacturers. And it is used for selecting the circuit breakers. This is also called MOP (Maximum overcurrent protection)

## Slide 9: Operation Range
Extended range of outdoor ambient temperature operation
-5˚C
+48˚C
Cooling mode range
-23˚C
+24˚C
Heating mode range
0 ˚C
5 ˚C
10 ˚C
15 ˚C
20 ˚C
25 ˚C
30 ˚C
35 ˚C
40 ˚C
45 ˚C
50 ˚C
-10˚C
-5 ˚C
-15˚C
-23˚C
55 ˚C
AF5300

## Slide 10: Operation Modes
Auto mode (default)
Cooling or Heating priority mode
Lock cooling mode
Lock heating mode
Voting priority
(Majorities’ requirement)
VIP priority
(default address No.63)
The outdoor unit only operates in heating mode
Outdoor unit operates according to ambient temp. (T4)
Heating If T4 < 13 °C, Cooling if T4 > 18 °C
Continue Last time operation if 13 T4  18
The outdoor unit only operates in cooling mode
During heating operation: If an indoor unit requests cooling, the outdoor unit stops and then restarts in cooling. During cooling operation: If an indoor unit requests heating, the outdoor units ignore the request and continue to run in cooling mode.
In voting priority mode, the outdoor unit operates in
whichever of heating and cooling modes is being
requested by the larger number of indoor units.
If the VIP indoor unit is operating, the
outdoor unit operates in the mode of the VIP indoor unit.
#63 Now the address can be changed
AF5300

## Slide 11: Compressor Technology
AF5300
Increased heating performance by 20% in average for outdoor temperatures below +7 °C
Wide running frequency 15~140Hz
Stable operation down to -23 °C (-25 °C for AF6300 Series )
Improved heating capacity at lower temperatures down to -15 °C
Vapor injection type scroll compressor also ensures efficient sub-cooling without loss during cooling operation
Vapor injection type compressor
Low-pressure refrigerant suction
Gas Vapor Injection
High-pressure refrigerant discharge
Common With AF6300

## Slide 12: Sub-Cooling Circuits
Improved cooling efficiency by 10%
Reduced refrigerant pressure loss
Lower refrigerant flow noise
Better refrigerant distribution
2nd Stage
Plate HEX
1st Stage
HEX
For more information
please refer to the EDBs and SMs
AF5300
Common With AF6300
Notes: New outdoor units use 2-stage sub cooling technology to cooling down the refrigerant. First, Outdoor heat exchanger cooling down the refrigerant and then the system will bypass a small amount of refrigerant and go across a auxiliary EXV, these a small amount of refrigerant will change to low pressure and low temperature state and further cooling down the main refrigerant, guaranteeing the whole refrigerant going to the indoor units is in pure liquid state. The liquid refrigerant flow has less pressure loss, lower noise and better refrigerant distribution

## Slide 13: Efficient Refrigerant Control
Floating refrigerant temperature ensures comfort and efficiency. The evaporation (in cooling) and condensation temperatures (in heating) are automatically adjusted according to indoor and outdoor ambient temperature.
Evaporating temperature (floating) ℃
Chart: 
| 17 | 32
区域 1 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
区域 2 | 13 | 11.9 | 11 | 10.2 | 9.5 | 8.9 | 8.4 | 7.9 | 7.5 | 7.1 | 6.8 | 6.6 | 6.4 | 6.2 | 6.1 | 6
Te (fix)
Te
17℃ 32℃
Indoor Temperature
Top efficiency
Quick reaction speed
Balance mode
Perfect balance:
Top efficiency on the transition seasons and quick reaction in summer, hottest days.
AF5300
Common With AF6300
Notes: Depends on the ambient temperature, the target evaporating temp changes automatically. For example, when the ambient temp is low, like in the transition season, lower capacity is required, higher evaporating temp brings higher energy efficiency. When the ambient is high, like in summer, higher capacity is required, lower evaporating temp brings quick reaction speed to cooling and larger cooling capacity. In normal seasons, the evaporating temp is adjusted automatically to balance the comfort and energy efficiency.

## Slide 14: Patented Fan Design
4+4 spectrogram
3+4 Spectrogram
Unique design :3+4
Patented
Conventional design:4+4
For models 18-20-22 HP
AF5300
Common With AF6300

## Slide 15: Simplified Electronical Circuit
DC filter board, AC contactor, inverter module and compressor drive circuits are integrated to one compressor inverter drive board.
Integrated design reduces wiring connections at PCB and offers more reliable PCB.
old
new
AF5300
Common With AF6300

## Slide 16: Easy Check & Maintenance
The bottom layer can be easily accessed through rotatable PCB in case maintenance is needed.
For more information
please refer to the EDBs and SMs
Bottom layer of the electric control box
Rotatable upper PCB of the electric control box
AF5300
Common With AF6300

## Slide 17: Safety Cover
To prevent direct access to high voltage areas at PCB, a safety cover has been adapted.
AF5300
Common With AF6300

## Slide 18: IPM Cooling Technology
Double U-shape refrigerant pipe decreases the IPM temperature and ensures reliable operation
IPM : Intelligent power module
For more information
please refer to the EDBs and SMs
AF5300
Common With AF6300

## Slide 19: Equal Aging
In systems with multiple outdoor units, outdoor unit duty cycling is used to equalize the compressor life span and balance the oil at compressors.
AF5300
Common With AF6300

## Slide 20: Combination
There is no more oil balance piping needed at site.
No need for oil balance pipe
AF5300
Common With AF6300

## Slide 21: Automatical Ref. Charging
VRF system can be charged with the necessary amount of refrigerant automatically
Automatic charging* decide appropriate amount of refrigerant to be chared to piping system
Conventional manual refrigerant charge:
Calculation of additional refrigerant charging volume
Measuring the weight of the cylinder
Charge system with additional refrigerant
* Setting is done via dip-switch at outdoor unit pcb
For more information
please refer to the EDBs and SMs
AF5300
Common With AF6300

## Slide 22: ESP Flexibility
Outdoor unit fans can overcome external static pressure up to 40 Pa* , for AF6300 Ex.Static Pressure up to 80 Pa*
Types of application needs ;
  Floor by floor installation inside building with louver appl.
  Long air-duct applications
AF5300
Setting is done via dip-switch at outdoor unit pcb
Standart setting is 0 Pa
0,10,20,30,40 (Can be selected via dip-switch)
AF5300
Common With AF6300
Setting is done via dip-switch at outdoor unit pcb
Standart setting is 0 Pa
0,20,40,60,80
(Can be selected via dip-switch)
AF6300

## Slide 23: Auto Dust Clean
Self-clean
Dust clean function enables outdoor units heat exchanger to clean itself and prevent from dust
Maintain system operate at high efficiency like installed and running as first day and ensure reliability
* Setting is done via dip-switch at outdoor unit pcb
For more information
please refer to the EDBs and SMs
AF5300
Common With AF6300

## Slide 24: Auto Snow Blowing
Auto snow function enables outdoor units to be covered with snow
A special program at software controls fan(s) to start and work for a period to avoid snow covering outdoor unit
* Setting is done via dip-switch at outdoor unit pcb
For more information
please refer to the EDBs and SMs
AF5300
Common With AF6300

## Slide 25: Check-Box
The digital display on data transfer module displays the same information as the digital display on main PCB.
Main functions :
System check, Sync LED, Auto snowblowing setting,
Data acquisition, Fault data storage, Data reading,
Menu mode setting
For more information
please refer to the EDBs and SMs
AF5300
Common With AF6300

## Slide 26: Capacity Adjustment
It is possible to set the capacity output from 100% to 40% in case needed (eg. During power generator is running)
Digital display code | Menu mode | Remarks
n41 | Power limitation mode 1 | 100% capacity output
n42 | Power limitation mode 2 | 90% capacity output
n43 | Power limitation mode 3 | 80% capacity output
n44 | Power limitation mode 4 | 70% capacity output
n45 | Power limitation mode 5 | 60% capacity output
n46 | Power limitation mode 6 | 50% capacity output
n47 | Power limitation mode 7 | 40% capacity output
40%
Minimum
capacity output
Maximum
capacity output
50%
60%
70%
90%
80%
100%
For more information
please refer to the EDBs and SMs
AF5300
Common With AF6300

## Slide 27: Silent Modes
AF5300
Common With AF6300
Night silent mode :
Is activated X hours after the peak daytime temperature, and is deactivated after Y hours
Silent Mode :
Maximum fan speed is limited
Super Silent Mode :
Maximum fan speed and maximum compressor frequency is limited
Mode | Description | Sound reduction (dBA) | Capacity Output %
0 | Night silent time 6h/10h | 8 dB(A) lower | 90%
1 | Night silent time 6h/12h | 8 dB(A) lower | 90%
2 | Night silent time 8h/10h | 8 dB(A) lower | 90%
3 | Night silent time 8h/12h | 8 dB(A) lower | 90%
4 | No silent mode | - | 100%
5 | Silent mode 1 | 8 dB(A) lower | 90%
6 | Silent mode 2 | 9 dB(A) lower | 85%
7 | Silent mode 3 | 10 dB(A) lower | 80%
8 | Super silent mode 1 | 12 dB(A) lower | 75%
9 | Super silent mode 2 | 14 dB(A) lower | 65%
10 | Super silent mode 3 | 16 dB(A) lower | 55%
11 | Super silent mode 4 | 18 dB(A) lower | 45%
Mode | Description | Sound reduction (dBA) | Capacity Output %
0 | Night silent time 6h/10h | 4 dB(A) lower | 85%
1 | Night silent time 6h/12h | 4 dB(A) lower | 85%
2 | Night silent time 8h/10h | 4 dB(A) lower | 85%
3 | Night silent time 8h/12h | 4 dB(A) lower | 85%
4 | No silent mode | - | 100%
8 | Silent mode | 4 dB(A) lower | 85%
A | Super silent mode | 8 dB(A) lower | 75%
F | Reserved |  | 
AF5300 Silent mode options
AF6300 Silent mode options

## Slide 28: Back-Up Operation
AF5300
In a multi-unit system, if one module fails, other modules can provide backup operation.
Compressor is running
Compressor at stand-by
Compressor broken
Remark : This function is valid where multi outdoor units are combined at installation and back-up can be applied manually at installation site by installer.
Common With AF6300
It is possible to set the compressor to run as emergency operation for 4 days if there are 2 compressors in one unit allowing time for maintenance or repair.
Compressor back up operation in case of cascaded application of outdoor units

## Slide 29: Pump Up&Down Operations
AF5300
Common With AF6300
Refrigerant can be recycled to ;
outdoor units
indoor units
outdoor units running normal
This function is for maintenance and commissionnig , stop valve must be closed manually.
Refrigerant recycle to outdoor units
Refrigerant re-cycle to indoor units and to outdoor units running normal

## Slide 30: Maintenance Mode
AF5300
Common With AF6300
Maintenance feature allows shutdown of a vrf indoor unit without shutting down whole VRF system.
This feature allows easy & flexible maintenance as remaining indoor units continue to operate.
Normally if outdoor unit finds more than 1 indoor unit missing for 3 minutes, then H7 protection error occurs.
In maintenance mode, unit will not check the indoor unit quantity. Then installer have enough time for maintenance of indoor unit. This feature is valid only for electrical problems.
Remarks :
Activated via master outdoor unit PCB. Valid for 3 hours.
This function is not used for refrigerant side maintenance & problems.

## Slide 31: Another Advantages
AF5300
Feature | Benefit | Reason why
Anti-vibration technology | Low noise level | New anti-vibration technology, soft metal pipe is used for compressor suction and injection. High quality rubber is used.
Auto refrigerant check | Reliable operation | Lack of refrigerant or over-charged refrigerant can be displayed at outdoor unit pcb.
Common With AF6300

## Slide 32: Product Line up & Feature
Af5300 ODU ( 2 Pipe)
AF6300 ODU ( 3 Pipe)
Ahu-Kit D
HydroBox
ERV unit
Controllers

## Slide 33: Product Line-Up
AF6300
6 different models with a capacity up to 50 kW
Combination of 3 outdoor units up to 150 kW
Combination ratio min %50 ~ max %200
380-415V, 50Hz, triphase
CE and Eurovent
HP | 8,10,12 | 14,16,18 | 20  36 | 38  54
kW | 22.4, 28, 33.5 | 40, 45, 50 | 56  100 | 106  150
ID |  |  |  | 
System | total combination ratio | Allowed combination ratio |  | 
 |  | VRF indoor units | Hydro box | AHU Kit
VRF indoor units only | 50%~200% (Single) 50%~150% (2 units combination) 50%~130% (3 units combination) | 50%~200% (Single) 50%~150% (2 units combination) 50%~130% (3 units combination) | / | /
VRF indoor units + HT hydro box | 50%~200% | 50%~130% | 0%~100% | /
VRF indoor units + AHU kits | 50%~100% | 50%~100% | / | 0%~50%

## Slide 34: Combination Table
AF6300
System capacity |  | Number of units | Modules1 |  |  |  |  |  | Outdoor unit Branch joint kit2
kW | HP |  | 8 | 10 | 12 | 14 | 16 | 18 | 
22.4 | 8 | 1 | ● |  |  |  |  |  | —
28.0 | 10 | 1 |  | ● |  |  |  |  | 
33.5 | 12 | 1 |  |  | ● |  |  |  | 
40.0 | 14 | 1 |  |  |  | ● |  |  | 
45.0 | 16 | 1 |  |  |  |  | ● |  | 
50.0 | 18 | 1 |  |  |  |  |  | ● | 
56.0 | 20 | 2 |  | ●● |  |  |  |  | AF-BJRO 02
61.5 | 22 | 2 |  | ● | ● |  |  |  | 
68.0 | 24 | 2 |  | ● |  | ● |  |  | 
73.5 | 26 | 2 |  |  | ● | ● |  |  | 
78.5 | 28 | 2 |  |  | ● |  | ● |  | 
83.5 | 30 | 2 |  |  | ● |  |  | ● | 
90.0 | 32 | 2 |  |  |  |  | ●● |  | 
95.0 | 34 | 2 |  |  |  |  | ● | ● | 
100.0 | 36 | 2 |  |  |  |  |  | ●● | 
107.0 | 38 | 3 |  |  | ●● | ● |  |  | AF-BJRO 03
112.0 | 40 | 3 |  |  | ●● |  | ● |  | 
118.5 | 42 | 3 |  |  | ● | ● | ● |  | 
123.5 | 44 | 3 |  |  | ● |  | ●● |  | 
130.0 | 46 | 3 |  |  |  | ● | ●● |  | 
135.0 | 48 | 3 |  |  |  |  | ●●● |  | 
140.0 | 50 | 3 |  |  |  |  | ●● | ● | 
145.0 | 52 | 3 |  |  |  |  | ● | ●● | 
150.0 | 54 | 3 |  |  |  |  |  | ●●● | 
The combinations of units shown in the table are factory-recommended. Other combinations of units are also possible.
For systems with two or more outdoor units, outdoor units branch joints (sold separately) are required.

## Slide 35: Working Range
AF6300
Pure cooling mode: -15°C ~ 52°C DB
Main cooling mode (mixed mode): -15°C ~ 27°C DB
Pure heating mode: -25°C ~ 27°C DB
Main heating mode (mixed mode): -15°C ~ 27°C DB

## Slide 36: Design
Outdoor
Unit(s)
Joints
System is able to run for at cooling, heating or simultaneously
Higher efficiency compared to 2-pipe VRF due to heat recovery
Single piping system (3 pipe, liquid/high pres gas/low pres gas)
R-410A refrigerant
Individual setting as on/off, set temp, air flow adjustment in rooms
Centralised control availibility
System capacity increase with by combining outdoor units up to 3, reaching max. 150 kW rated cooling capacity in one system
Ducted type
indoor unit
Refrigerant piping
3 pipes
(main pipes)
Cassette type
indoor unit
Switch Box
(SBOX)
Air Cooled
Heat Recovery VRF System
High-wall type
indoor unit
Central
controller
Room
controller
Infrared
controller
Refrigerant piping
2 pipes
(after box)
AF6300

## Slide 37: Working Principle
A typical heat recovery system consists of outdoor unit(s), switch box (changeover box) and indoor units, as well the copper piping and joints
System offers high energy-saving efficiency by rejecting heat from the rooms to be cooled and effectively using it as a heat source for the rooms to be heated.
H
OFF
C
OFF
H
C
H
Heat rejection
Heat rejection
Heat release
Heat release
Internal transfer
Internal transfer
C : cooling mode
H : heating mode
3 pipes
2 pipes
2 pipes
2 pipes
2 pipes
2 pipes
3 pipes
3 pipes
3 pipes
AF6300

## Slide 38: Energy Specifications
System | Outdoor Unit |  |  |  | Current | 
 | Voltage (V) | Frequency (Hz) | Min. (V) | Max. (V) | MCA (A) | MFA (A)
AF6300A 22 C-3 | 380-415 | 50 | 342 | 440 | 24,0 | 32
AF6300A 28 C-3 | 380-415 | 50 | 342 | 440 | 25,2 | 32
AF6300A 33 C-3 | 380-415 | 50 | 342 | 440 | 26,4 | 32
AF6300A 40 C-3 | 380-415 | 50 | 342 | 440 | 33,1 | 40
AF6300A 45 C-3 | 380-415 | 50 | 342 | 440 | 33,1 | 40
AF6300A 50 C-3 | 380-415 | 50 | 342 | 440 | 40,8 | 50
MCA: Minimum Circuit Amps
MFA: Maximum Fuse Amps
Select the wire diameters separately for different unit models based on the relevant standards.
Maximum allowable voltage range variation between phases is 2%.
Select a circuit breaker that complies with the local laws and regulations.
Select the wire diameter and type of circuit breaker based on the table above where MCA is used to select the wire diameter, and MFA is used to select the current circuit breakers and residual current operation breakers
MCA (Minimum Circuit Ampacity)
It is used for conductor sizing to ensure that the wiring does not overheat under normal operating conditions. .
The minimum circuit ampacity (MCA) is the minimum wire size required for a field wired product. It is chosen to guarantee that the wiring will not overheat under the expected operating conditions.
The wire size takes into account the normal current draw, ageing of components and anticipated faults.
MFA (Maximum Fuse Amps)
This value is required for the protection of motor (fan motor), given by manufacturers.
And it is used for selecting the circuit breakers.
This is also called MOP (Maximum overcurrent protection)
AF6300

## Slide 39: Oil Return Logic
Three stage of oil control technology ensure outdoor unit’s compressor oil is always kept at a safe level, eliminating any compressor oil shortage problems.
  Compressor internal oil separation.
  High-efficiency centrifugal oil separator (with separation efficiency of up to 99%) ensures that oil is separated from the discharge gas and returned to the compressor.
  Auto oil-return program monitors the running time and system status to ensure reliable oil return.
AF6300

## Slide 40: Continous Heating
Remark : This function is valid where multi outdoor units are combined at installation
Normally, outdoor unit stops normal heating operation during defrost operation.
However, continuous heating operation feature makes it possible to perform defrosting while heating operation continues. In cascaded applications, (2 outdoor units or 3 outdoor units), units perform defrosting alternately. While one unit is performing defrosting, the other one continues heating.
Continuous Heating Operation
Normal Heating Operation
Heating
Heating
Continuous Heating Operation
Heating
Defrost
Heating
Defrost
AF6300

## Slide 41: Expanded HEX Area
In cooling or heating mode, for a multi-unit system, outdoor unit heat exchanger (HEX) and compressor are independently controlled to improve energy efficiency. This means even compressor of outdoor unit is not running, heat exchanger of this outdoor unit can be used for heat transfer. This function maximize outdoor units heat exchanger area and improves efficiency.
Compressor is running
Compressor at stand-by
Compressor is running
Compressor at stand-by
OTHER BRANDS
Remark : This function is valid where multi outdoor units are combined at installation
AF6300

## Slide 42: Refrigerant Control
Smart Automatic Refrigerant Temperature Control: The evaporating temperature (in cooling) and condensing temperature (in heating) are automatically adjusted according to both indoor and outdoor temperature to maximize the comfort and energy efficiency.
Also manual setting is possible at outdoor unit.
Tevap auto control C : 3, 6 (Default), 9
Tevap locking C : -3, 0, 3, 6, 9
Tcond auto control C : 42, 45, 48 (Default), 50
Tcond locking C : 44, 46, 48, 51
AF6300

## Slide 43: Communication Lines
Only one chain of 3-core connection cable is required for indoor unit, outdoor unit and centralized controller communication.
P Q E
P Q E
X Y E
X1 X2
X1 X2
X1 X2
X1 X2
P Q E
P Q E
P Q E
P Q E
For more information please refer to the installation manual
In case of outdoor units combination
1 : Master unit , 2 : Slave units
AF6300

## Slide 44: Easy Addressing
Outdoor unit can distribute addresses to indoor units automatically during commissioning.
Remote and wired controllers can be used to query or modify each indoor unit's address.
P Q E
P Q E
X1 X2
X1 X2
X1 X2
X1 X2
P Q E
P Q E
P Q E
P Q E
AF6300

## Slide 45: Remote Controls
Outdoor Unit Input / Output Dry Contact
Outdoor unit supports 12V input and 220V output dry contacts to extend functions.
For example, the input dry contact can achieve remote emergency stop function and output dry contact which can be connected to an alarm to achieve remote alarm function.
Remote Emergency Stop
Stop Signal, 12V input
Remote Alarm
Error Signal, 220V output
Normal run
Normal run
AF6300

## Slide 46: Product Line up & Feature
Af5300 ODU ( 2 Pipe)
AF6300 ODU ( 3 Pipe)
Ahu-Kit D
HydroBox
ERV unit
Controllers

## Slide 47: Models
AHU KIT -D
AHU Kit | 
Product Content | 
220 V, 50 Hz
Combination of 4 x AHU Kits is possible (up to 224 kW)
Type | AHU KIT 00 D | AHU KIT 01 D | AHU KIT 02 D | AHU KIT 03 D
kW | 2.2 ~ 9 | 9 ~ 20 | 20 ~ 36 | 36 ~ 56
PCB
EEV
Sensors
Controller

## Slide 48: Models
AHU KIT -D
Product is used for ventilation (Fresh air and exhaust air). It covers the ventilation needs within VRF projects and also can be used stand alone.
Product Number at SAP | EAN Number | Family | Product Name | Product Type | SAP Description
7733701731 | 4062321331726 | Accessory | NA | AHU KIT 00 D | AHU Kit, (2,2 - 9 kW)
7733701732 | 4062321331733 | Accessory | NA | AHU KIT 01 D | AHU Kit, (9 - 20 kW)
7733701733 | 4062321331740 | Accessory | NA | AHU KIT 02 D | AHU Kit, (20 - 36 kW)
7733701734 | 4062321331757 | Accessory | NA | AHU KIT 03 D | AHU Kit, (36 - 56 kW)
8750501740 | Spare part | Controller | NA | ARC AHU kit | Controller for AHU Kit
7739834425 | 4057749325778 | Accessory | NA | KIT-BJ 01 | Joint For AHU kit (20-46kW)
7739834426 | 4057749325785 | Accessory | NA | KIT-BJ 02 | Joint For AHU kit (46-66kW)
7739834427 | 4057749325792 | Accessory | NA | KIT-BJ 03 | Joint For AHU kit (66-135kW)
7739834428 | 4057749325808 | Accessory | NA | KIT-BJ 04 | Joint For AHU kit (>135kW)

## Slide 49: Working principle
AHU KIT -D
Use case: DX-AHU only
AHU kit
Option1
Wired controller
(factory supplied)
Option 2
3rd Party
DDC Controller
DX - AHU
VRF
Outdoor Unit
Gas pipe
Liquid pipe
Communication Wiring

## Slide 50: Working principle
AHU KIT -D
5 temperature sensors (T1, TA, T2A, T2 and T2B) and 5 extension wires in delivery scope
Installation location for temperature sensors:
Sensor | Description | Location
T1 | AHU return air temperature sensor | Installed at return air inlet of AHU
T2A | AHU evaporator inlet temperature sensor | installed at the inlet pipe of the evaporator
T2 | AHU evaporator intermediate temperature sensor | installed at the intermediate pipe of the evaporator
T2B | AHU evaporator outlet sensor | installed at the outlet pipe of the evaporator
TA | Supply air temperature sensor | installed in case supply air temperature control is needed

## Slide 51: Design
AHU KIT -D
Main pipes | L1,L2,L3
Branch joints | A,B
AHU Kits | N0,N1,N2
AHU Kit connection pipes | a1,a2,b1,b2,c1,c2
Gas pipes | a3,b3,c3
Option 1: One AHU kit is connected to one DX-coil
Max. Piping lengths
a2 ≤8 meters
b2 ≤8 meters
c2 ≤8 meters
Pipe diameters of AHU Kits (Liquid line):
Note:
1) The pipe L1 diameter is still related to outdoor unit, take the larger one for your selection.
2) The gas pipe should be confirmed according to the outdoor unit installation manual.
3) Branch joints should be confirmed according to the outdoor unit installation manual.
Heat Pump VRF Outdoor Unit
AF5300A
AF5300A C
MDCI
DX-coil 1
DX-coil 2
DX-coil 3

## Slide 52: Design
AHU KIT -D
Main pipes | L1,L2,L3,L4
Branch joints | A,B
AHU Kits | N0,N1,N2
AHU Kit connection pipes | a1,a2,b1,b2,c1,c2
Gas pipes | L5
Option 2: Several AHU kits are connected to one DX-coil
Max. Piping lengths
a2+L4 ≤8m
b2+L2+L4 ≤8m
c2+L2+L4 ≤8m
Pipe diameters of AHU Kits (Liquid line):
Joint selection :
Note:
1) The pipe L1 diameter is still related to outdoor unit, take the larger one for your selection.
2) The gas pipe should be confirmed according to the outdoor unit installation manual.
DX-coil
Heat Pump VRF Outdoor Unit
AF5300A
AF5300A C
MDCI

## Slide 53: Design
AHU KIT -D
Option 3: Connection at Heat Recovery VRF system

## Slide 54: Product Line up & Feature
Af5300 ODU ( 2 Pipe)
AF6300 ODU ( 3 Pipe)
Ahu-Kit D
HydroBox
ERV unit
Controllers

## Slide 55: Product Line up & Feature
Hydrobox AF-HB 140-1

## Slide 56: Product Line up & Feature
Controller
Smallest volume and weight in the industry
Hot water production up to 80C
Heat recovery at cooling from indoor units, free hot water
Outlet water temperature is from 25 C to 80C
Wide operating temperature range -20 C to +43C
No need for an auxiliary electric heater
Connection ratio up to 200%
Several hot water production scenarios
Several functions including disinfenction for legionella
Heat Recovery
VRF Outdoor Unit
SBOX
VRF indoor units
Hydro box
3-way valve
Underfloor heating
Water
tank
Domestic hot water
Rejected heat during cooling operation is used for heating and/or for domestic hot water at heat recovery vrf system
Hot Water Production
Cooling
Heating
System Schematic
Free heating & hot water production
+
Hydro box
For more information about hydro box applications,
Please refer to Hydro box product information presentation
Hydrobox AF-HB 140-1

## Slide 57: Hydraulics
Hydrobox AF-HB 140-1
The system has two compressors (ODU and Hydrobox) and two refrigerant circuits. In low temperature stage, it is a R-410A refrigerant cycle. R-410A absorbs the heat from environment and release heat energy to the plate heat exchanger within the hydro-box.
In high temperature stage, it is a R-134a refrigerant system. R-134a absorbs heat from R-410A and release heat energy to water.

## Slide 58: Hydraulics
Hydrobox AF-HB 140-1

## Slide 59: Scenario 1
Hydrobox AF-HB 140-1

## Slide 60: Scenario 2
Hydrobox AF-HB 140-1

## Slide 61: Scenario 3
Hydrobox AF-HB 140-1

## Slide 62: Scenario 4
Hydrobox AF-HB 140-1

## Slide 63: Scenario 5
Hydrobox AF-HB 140-1

## Slide 64: Scenario 6
Hydrobox AF-HB 140-1

## Slide 65: Product Line up & Feature
Af5300 ODU ( 2 Pipe)
AF6300 ODU ( 3 Pipe)
Ahu-Kit D
HydroBox
ERV unit
Controllers

## Slide 66: Models
ERV
SAP No | EAN No | Type | Product Type | SAP Description
7733700991 | 4062321204099 | ERV | ERV 300-1 | ERV Unit, 300m3/h
7733700992 | 4062321204105 | ERV | ERV 400-1 | ERV Unit, 400m3/h
7733700993 | 4062321204112 | ERV | ERV 500-1 | ERV Unit, 500m3/h
7733700994 | 4062321204129 | ERV | ERV 800-1 | ERV Unit, 800m3/h
7733700995 | 4062321204136 | ERV | ERV 1000-1 | ERV Unit, 1000m3/h
ERV is used for ventilation (Fresh air and exhaust air). It covers the ventilation needs within VRF projects and also can be used stand alone.

## Slide 67: Working principle
ERV
Energy saving ventilation using indoor heating, cooling and moisture
Ideal solution for ventilation next to VRF cooling & heating system for shops, restaurants or offices requiring maximum floor space for furniture, decorations
Wide range : Air flow rate from 300 m³/h up to 1.000 m³/h
Thermal efficiency up to 80% (300 m³/h unit)
Special heat exchange element made by high efficient paper
In accordance with EU regulations
Built-in class F7 filter for air supply side and class M5 filter for exhaust air side ( x >%80 0,4µm)
Built-in CO2 sensor at unit ensures indoor air quality
Free cooling is possible when outdoor temperature is below indoor temperature (f.e. during night time or at pre-seasons)
Several operation modes : Energy recovery, By-pass, Auto, Free-cooling
Reduced energy consumption with DC fan motors
Free dry contacts to connect fire alarm, electrical heater

## Slide 68: Installation
ERV
Return air
Exhaust air
Exhaust
fan
Supply
fan
Heat
Exchanger
By-pass damper
e-box
Air filter at
supply side
Access panel
Air filter at
exhaust side
Fresh air
Supply air
New heat exchanger element is produced from a special paper that is processed with chemical treatment and ensures optimum results in temperature, humidity and cooling recovery.

## Slide 69: Controller
ERV
Stand alone operation with ARC
(4)
ERV…1
Control with ARC and ACC MT
(1)
(2)
(3)
(1)
(2)
(5)
(4)
(3)
ERV
(6)
(7)
(8)
VRF IDU…1
ERV…2 ( 16 units)
Mixed operation with VRF indoor units
(1)
(2)
(5)
(4)
(3)
(6)
(7)
(8)
(9)
VRF IDU…1
ERV…2 ( 16 units)
Control via ACC MT only
(5)
(4)
(6)
(7)
(8)
(9)
ARC C-1 (Slave)
ARC C-1 (Master)
X1-X2
ERV Unit
PQE (IDU-ODU connection)
VRF outdoor unit
XYE (ODU-ACC connection)
ACC MT central controller
VRF indoor unit
D1-D2 group control
(10)
(2)
(3)
VRF IDU…1

## Slide 70: Installation
ERV
In summer days, high temperature outdoor air gets cooled by indoor exhaust air; in winter, low temperature outdoor air gets heated by indoor exhaust air. So the energy contained in exhaust air can be reclaimed and energy efficiency gets improved.
In mild climate areas or pre-seasons, when temperature and humidity difference between indoor and outdoor ambient is small, the unit works as a conventional ventilation fan. Both supply fan and exhaust fan work at the same speed (Hi/mid/low/auto).
The controller chooses heat exchange mode or bypass mode according to the temperature difference between outdoor and indoor ambient temperature. Fan speed must be auto fan speed – ERV is controlled according to C02 level When |T1-T4|≥5℃, heat exchange mode When T1-T4|＜5℃, by pass mode.Minimum change interval is 1 hour.
Fan speed can be set to L/M/H When T1<T4, heat exchange mode is active When T1≥T4, free-cooling mode is activated in bypass mode Minimum change interval is 1 hour.
Energy Recovery Mode
By-pass Mode
Auto Mode
T1: Indoor ambient temperature
T4:Outdoor ambient temperature
Free Cooling Mode

## Slide 71: Energy saving (Example winter)
ERV
Let’s select ERV 1000-1 for a project in Istanbul and calculate the amount of energy saved in winter conditions.
Location : Istanbul, winter season average outdoor air temp : +5ºC (DB)
Temperature efficiency of ERV 1000-1 @110Pa, 75%
Air flow rate (V) : 1000 m³/h
Indoor design temperature (Ti) : +20ºC
Average seasonal outdoor temp (To) : +5ºC
Density of air (r) : 1,26kg/m³
Specific heat (Cp) : 1,004kJ/kg.K
ERV unit efficiency (eff) : % 75
Supply air temperature of ERV (Ts) : Ts=To + eff x (Ti –To) = 5 + 0,75 (20-5) = 16,25ºC
Energy needed to heat up fresh air supplied to room at room heating conditions :
Q = V x r x Cp (Ti - Ts) = 1000 x 1,26 x 1,004 x (20-5) / 3600 = 5,3 kW
Energy needed in case ERV unit is used :
Q = V x r x Cp (Ti - Ts) = 1000 x 1,26 x 1,004 x (20-16,25) / 3600 = 1,3 kW
Energy saved by using ERV = 5,3 – 1,3 = 4 kW
Energy saved for 1 winter season, (office project) : 6m x 20d x 8hrs x 4kW = 3840 kW
(Oct-March, 6m ; Daily opr. 8hrs, 5 days/wk)

## Slide 72: Product Line up & Feature
Af5300 ODU ( 2 Pipe)
AF6300 ODU ( 3 Pipe)
Ahu-Kit D
HydroBox
ERV unit
Controllers

## Slide 73: Controllers
ARC C IR
ARC C-1 & H-1
ACC – MT
Accessories
AC – CM
AC - XYE

## Slide 74: Controllers
ARC C IR
ARC C-1 & H-1
ACC – MT
Accessories
AC – CM
AC - XYE

## Slide 75: Features
Dimension (GxYxD) mm | 170x47x25
On / Off Control | 
Modes (Auto,Cooling,heating, dry, fan) | 
Temperature setting | 0.5°C
7 Speed Fan Control | 
Auto Swing | 
5 step swing control | 
Address Setting | 
Follow me | 
Eco Mode | 
Show Room Temp. | 
Sleep Mode | 
Display Shut Off | 
Keyboard / Child Lock | 
Background Light | 
Timer | 
ARC IR
ARC IR – Remote Controller

## Slide 76: Features
ARC IR - Remote Controller
Internal | TT-CA/PRM | 03/07/2018
© Robert Bosch GmbH 2017. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Internal | TT-CA/PRM | 03/07/2018
7 Step Fan Speed
NEW
NEW
NEW
NEW
Eco Mode
Turn of LED light of Indoor Unit
Follow-me function
With the follow me function, the indoor unit responds to the temperature measured by the temperature sensor built-in to the wireless remote controller, rather than the temperature sensor in the indoor unit itself, enabling more precise control of the temperature in the user's immediate environment.

## Slide 77: Features
ARC IR - Remote Controller
Internal | TT-CA/PRM | 03/07/2018
© Robert Bosch GmbH 2017. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Internal | TT-CA/PRM | 03/07/2018
5 step swing louver
NEW
NEW
NEW
NEW
Timer ON & Timer OFF
Sleep Mode
Key Lock Function
The air is comfortably spread upwards and downwards thanks to the 5-step swing louver that can be programmed via the controller.
Sleep mode logic, after receive the 'sleep mode' command, the unit will work in cooling/heating mode with auto fan. After 8 hours, or receive the OFF command, or switch to other mode, the unit will quit silent mode

## Slide 78: Controllers
ARC C IR
ARC C-1 & H-1
ACC – MT
Accessories
AC – CM
AC - XYE

## Slide 79: Button Functions
ARC C-1 & H-1 - Wired Controllers
Easy Handling
Clear-text information line,
context sensitive
Advanced Functions* Away Mode, Eco
Sleep, Power Heat & Power Cool
Wall Socket Lock
4
2
7
1
3
7 Speed Fan New in market
Clock & Date
Easy Usage
Context-sensitive help function
5
Schedule* New Schedule function,
Bosch property
6
8
2 wire / 2 way communication 2 wire terminal type connection
* Some features are only available with ARC C-1

## Slide 80: Features
ARC C-1 & H-1 - Wired Controllers
7 Step Fan Speed
NEW
NEW
NEW
NEW
2 wire / bi-directional com.
Away Mode & Auto-changeover
Schedules
Weekly and Seasonal Schedules
Daily Intervals (max 3)
User defined schedules (max 3)
The wired controller can query the system operating parameters thanks to the new bi-directional communication functionality. In addition, settings including static pressure, cold draft prevention and temperature compensation can be configured on the wired controller
Heat
Cool
28 C
24 C
Heat
Cool
28 C
24 C

## Slide 81: Features
ARC C-1 & H-1 - Wired Controllers
NEW
NEW
Away Mode
Heat
Cool
28 C
24 C
Heat
Cool
28 C
24 C
Auto-changeover
Away-Mode is enabled for ARC H-1. The function now interlink with the Hotelcard / Window-Door Card. Options for away mode:
1. Always on
2. Always off
3. Only active if Hotelcard is plugged out
When this feature is activated, ARC always check the room temperature and it is lower or upper than defined temperature, unit runs by itself for ensuring to keep temperature in defined range.
This feature will be activated when auto mod selected by controller .
Set the temperature band starting from the set temperature, within which Auto Mode changeover between cooling and heating takes place.
Adjustment range: 2 ... 4 ... 6 °C e.g. Setting 4 °C: If the set temperature is exceeded by 2 °C, Auto Mode switches to cooling. If the temperature falls 2 °C below the set temperature, Auto Mode switches to heating

## Slide 82: Features
ARC C-1 & H-1 - Wired Controllers
5 step swing louver
NEW
NEW
NEW
NEW
Turbo Heat & Cool
Sleep Mode
Monitor System Parameters
The air is comfortably spread upwards and downwards thanks to the 5-step swing louver that can be programmed via the controller.
Set flexible time between 2 – 10 hrs. During that time fan speed level will be changed to “auto” and set temperature will be increased/decreased to improve sleep quality and to reduce noise. After the timer has been elapsed the IDU will be turned off

## Slide 83: Features
ARC C-1 & H-1 - Wired Controllers
Normally open contact, change before the application to normally closed contact
Can be linked with hotel card switch, door & window switch
option 1: card plugged out : AC is off and ARC is locked
card plugged in again: AC is OFF, ARC is unlocked, user need to turn AC with ARC.
option 2: card plugged out : AC is off and ARC is locked
card plugged in again: AC is ON, ARC is unlocked, user response is not needed.

## Slide 84: Wiring
ARC C-1 & H-1 - Wired Controllers
Single Use cases
Twin Use cases
PQE
X1-X2
X1-X2
PQE
X1-X2
X1-X2
X1-X2
Master
Slave
PQE
D1-D2
….16
X1-X2
X1-X2
Group Use case up to 16
Master
Slave

## Slide 85: Controllers
ARC C IR
ARC C-1 & H-1
ACC – MT
Accessories
AC – CM
AC - XYE

## Slide 86: Key Functions
ACC MT - Central Controller
Floor Plan Manager
Local Remote (Web Access)
E-mail alerts
Extendable Solution
One device for various application connected up to 256 Indoor Units
4
2
7
1
3
Internet connectivity New in market: remote update
POE (Power Over Ethernet)
Easy Usage
Dashboard and tile view
5
Schedule New Schedule function, Bosch property
6
8
Monitor System Parameters

## Slide 87: Features
ACC MT - Central Controller
Different View Options for Operation
Dashboard & Tile View
Native Languages for all markets
  Icon View
English, Turkish, Spanish, German, Portuguese, French, Polish, Russian, Kazakh,
Quick Access to menus
Monitor system overview
Clear information
Floor Plan
  List View

## Slide 88: Features
ACC MT - Central Controller
Remote Update
Floor Plan Manager
Manual on device
  either over the Internet (remote software update)
  or locally via an USB stick
Allocate indoor units on floor plan
  Context sensitive manual on device in local language
Monitor System Parameters

## Slide 89: Features
ACC MT - Central Controller
Schedules
Weekly schedules
Seasonal schedules
Exception management (bank holidays etc.)
Fault and event history
Fault history
500 latest error
Group Editor
Grouping Indoor Units
Renaming Indoor Units
Permission Levels
Low-Mid-High permission levels
User Level
Expert Level
Admin

## Slide 90: Features
ACC MT - Central Controller
Local Remote (Web Access)
Software Update
Done
Extendable Solution
Standard Product
+
AC-EXP
Expansion kit
Extended Solution
LAN /
Wi-Fi
PC (via LAN)
LAN
64 IDUs
256 IDUs
E-Mail Alerts
Internet-standard SMTP
E-mail
Done
POE (Power Over Ethernet)
State-of-the-art one-cable connection providing
  Ethernet data
  Power supply
Software Update

## Slide 91: Features
ACC MT - Central Controller
Robust Hardware
Superior 10.1” display and touch
State-of-the-Art commercial-grade DualCore processor platform (ARM Cortex A9)
1 GB of low-power RAM
2 GB of enhanced flash storage (extended life time)
  IPS for visibility from all angles incl. optical bonding to further enhance image quality
  Capacitive touch interface for tablet-like usability

## Slide 92: Wiring
ACC MT - Central Controller
Air Center Control
Max. 256 IDUs, 10”
Power Supply
LAN /
Wi-Fi
Local connectivity only
Max. 3 ODUs per system,
max. 8 systems per X,Y,E
= Max. 96 ODUs
Max. 64 IDUs per system, AND max. 256 IDUs in total
P,Q,E
2-pipe V6 systems
PC (via LAN)
ODUs
IDUs
Room Controller
Wired (2-wire) X1-X2
ARC C IR
Wired V6
(XYE - RS485)
1 RS-485 for main device
3 add. RS-485 via Exp. Board
Service
End User
End User
Installer
Service
Installer
LAN
Optional in case of PoE being used
IDU – In-Door Unit
ODU – Out-Door-Unit
IR – Infra-Red

## Slide 93: Wiring
ACC MT - Central Controller
ONE XYE PORT = 64 IDUs (MAX)
1 port supports maximum 8 refrigerant system
ACC Standard Product = 1 XYE ports
Note: Manual addressing would be needed for maximum connectivity
One XYE port
One XYE port
Port 3 ……………. 64 IDUs
Port 4 ……………. 64 IDUs
Port 2
ONE XYE PORT = 64 IDUs (MAX)
ACC Standard Product = 1 XYE port
1 port supports maximum 8 refrigerant system
With expansion kit : 4 XYE ports
Standart Product
Extended Product

## Slide 94: Gateway Types & Capabilities
ACC – MOD -1
ACC – BAC -1
ACC – LON -1

## Slide 95: Product Information
ACC MOD-1 -Modbus Gateways
Compatible with Air Flux 5300 A, Air Flux 6300 A, MDCI (AC-CM), AC-XYE, AC-CM, AF-1 Indoor Units, ERV*, AF-HB (Hydro-box),new AHU KIT
Offices, shops, hotels, residences where integration to building managements systems are required.
Product Group:
Gateway for VRF Line Up
Product Type: ACC MOD-1
WEU (SP, PT, PL, GB, DE, FR, IT) +CL
EEU (TR, RU, KZ, UA, RO, HR, TN, KE, RW, TZ, UG, SC)
ACC MOD-1
* Note: Lonworks gateway is not compatible with the ERV units.
Scope Summary / Major Requirements
Secure Gateways released based on Bosch Security Process
Compatibility of Gateways with new VRF 3 pipe systems

## Slide 96: Wiring
ACC MOD-1 -Modbus Gateways
© Robert Bosch GmbH 2017. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Port quantity: 1
Max IDU per port: 64
Max ODU per port: 24
Max IDU per gateway: 64
Max ODU per gateway: 24
Max system per gateway: 8
Only 8 refrigerant system
XYE
Option 1
Modbus RTU
Option 2
Modbus TCP
TTNR | Product Type | Product Description | EAN Number
7-733-701-754 | ACC MOD-1 | Modbus Gateway | 4062321359850
* 12 V power supply (in package)

## Slide 97: Gateway Types & Capabilities
ACC – MOD -1
ACC – BAC -1
ACC – LON -1

## Slide 98: Product Information
ACC-BAC -1 Bacnet Gateway
Compatible with Air Flux 5300 A, Air Flux 6300 A, MDCI (AC-CM), AC-XYE, AC-CM, AF-1 Indoor Units, ERV*, AF-HB (Hydro-box),new AHU KIT
Offices, shops, hotels, residences where integration to building managements systems are required.
Product Group:
Gateway for VRF Line Up
Product Type: ACC BAC-1
WEU (SP, PT, PL, GB, DE, FR, IT) +CL
EEU (TR, RU, KZ, UA, RO, HR, TN, KE, RW, TZ, UG, SC)
ACC BAC-1
Scope Summary / Major Requirements
Secure Gateways released based on Bosch Security Process
Compatibility of Gateways with new VRF 3 pipe systems

## Slide 99: Wiring
© Robert Bosch GmbH 2017. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
© Robert Bosch GmbH 2017. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
© Robert Bosch GmbH 2017. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
© Robert Bosch GmbH 2017. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Up to
8 refrigerant systems
Up to
8 refrigerant systems
Up to
8 refrigerant systems
Up to
8 refrigerant systems
Port quantity: 4
Max IDU per port: 64
Max ODU per port: 24
(one port up to 8 systems)
Max IDU per gateway: 256
(one port up to 8 systems)
Max ODU per gateway: 96
(one port up to 8 systems)
Max system per gateway: 32
(one port up to 8 systems)
TTNR | Product Type | Product Description | EAN Number
7-733-701-753 | ACC BAC-1 | Bacnet Gateway | 4062321359843
* External power supply
ACC-BAC -1 Bacnet Gateway

## Slide 100: Gateway Types & Capabilities
ACC – MOD -1
ACC – BAC -1
ACC – LON -1

## Slide 101: Product Information
ACC LON -1 Lonworks Gateway
Compatible with Air Flux 5300 A, Air Flux 6300 A, MDCI (AC-CM), AC-XYE, AC-CM, AF-1 Indoor Units, AF-HB (Hydro-box),new AHU KIT
Offices, shops, hotels, residences where integration to building managements systems are required.
Product Group:
Gateway for VRF Line Up
Product Type: ACC LON-1
WEU (SP, PT, PL, GB, DE, FR, IT) +CL
EEU (TR, RU, KZ, UA, RO, HR, TN, KE, RW, TZ, UG, SC)
ACC LON-1
* Note: Lonworks gateway is not compatible with the ERV units.
Scope Summary / Major Requirements
Secure Gateways released based on Bosch Security Process
Compatibility of Gateways with new VRF 3 pipe systems

## Slide 102: Wiring
ACC LON -1 Lonworks Gateway
© Robert Bosch GmbH 2017. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
© Robert Bosch GmbH 2017. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
© Robert Bosch GmbH 2017. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
© Robert Bosch GmbH 2017. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
© Robert Bosch GmbH 2017. All rights reserved, also regarding any disposal, exploitation, reproduction, editing, distribution, as well as in the event of applications for industrial property rights.
Port quantity: 1
Max IDU per port: 32
Max ODU per port: 24
Max IDU per gateway: 32
Max ODU per gateway: 24
Max system per gateway: 8
Up to
8 refrigerant systems
XYE
XYE
Up to 32 indoor units
TTNR | Product Type | Product Description | EAN Number
7-733-701-755 | ACC LON-1 | Lonworks Gateway | 4062321359867
* External power supply

## Slide 103: Thanks for your Time